{"text_format":"1","workbook":"xlsx","n_sheets":12,"sheets":["Projekt węzła","Dane wejściowe","Wymienniki CWU","Arkusz3","PN-C.O.","PN-NWP","PN-C.W.U.","Wymienniki CO","HEX","ZB","NWP","gestosc wody"],"not_rendered":{"charts":0,"images":8,"macros":1,"external_links":1,"defined_names":0,"comments":3,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Projekt węzła","index":0,"n_rows":742,"n_cols":10,"rows_kept":742,"cut":false,"hidden":false,"merged":[[267,0,267,9],[310,0,310,9],[354,0,354,9],[398,0,398,9],[371,0,371,3],[709,5,709,6],[415,0,415,5],[416,0,416,5],[707,5,707,6],[707,7,707,8],[708,5,708,6],[708,7,708,8],[707,0,707,3],[319,7,319,8],[334,7,334,8],[708,0,708,3],[412,0,412,8],[320,7,320,9],[325,0,325,9],[336,0,336,3],[335,7,335,9],[400,0,400,8],[402,0,402,3],[403,0,403,5],[321,0,321,3],[414,0,414,3],[369,0,369,4],[740,0,740,3],[741,0,741,3],[713,0,713,8],[734,0,734,3],[735,0,735,3],[736,0,736,3],[738,2,738,3],[739,2,739,3],[737,5,737,6],[737,7,737,8],[716,0,716,3],[717,0,717,3],[718,0,718,3],[729,0,729,3],[732,0,732,3],[733,0,733,3],[736,5,736,6],[736,7,736,8],[729,5,729,6],[726,7,726,8],[706,0,706,9],[729,7,729,8],[732,5,732,6],[732,7,732,8],[740,5,740,8],[741,5,741,8],[733,5,733,6],[733,7,733,8],[734,5,734,6],[734,7,734,8],[735,5,735,6],[735,7,735,8],[728,0,728,3],[709,0,709,3],[710,0,710,3],[711,0,711,3],[712,0,712,3],[714,0,714,4],[726,0,726,3],[727,0,727,3],[709,7,709,8],[719,0,719,3],[720,0,720,3],[710,5,710,6],[727,5,727,6],[727,7,727,8],[728,5,728,6],[728,7,728,8],[726,5,726,6],[723,0,723,3],[725,0,725,3],[715,0,715,3],[725,5,725,6],[725,7,725,8],[710,7,710,8],[711,5,711,6],[711,7,711,8],[719,5,719,6],[719,7,719,8],[0,0,0,9],[54,0,56,9],[75,0,76,9],[77,0,77,9],[78,0,79,9],[90,0,92,9],[59,0,60,9],[61,0,74,9],[41,0,42,9],[5,0,6,9],[105,0,115,9],[222,0,223,9],[235,0,236,9],[238,0,239,9],[2,0,3,9],[162,0,166,9],[181,0,185,9],[195,0,196,9],[198,0,199,9],[201,0,202,9],[204,0,206,9],[123,0,124,9],[148,0,149,9],[152,0,153,9],[190,0,192,9],[159,0,161,9],[116,0,120,9],[127,0,128,9],[186,0,187,9],[208,0,212,9],[134,0,139,9],[225,0,226,9],[229,0,231,9],[227,0,228,9],[692,4,692,6],[692,7,692,8],[703,1,703,8],[615,1,615,8],[662,1,662,8],[418,0,418,8],[420,0,420,3],[421,0,421,5],[422,0,422,5],[424,0,424,3],[426,0,426,5],[425,0,425,5],[530,0,530,9],[531,0,531,9],[574,0,574,9],[575,0,575,9],[499,0,499,9],[442,0,442,9],[490,0,490,4],[491,0,491,4],[493,0,493,4],[593,1,593,5],[603,4,603,6],[603,7,603,8],[486,0,486,9],[488,0,488,9],[454,0,454,9],[404,0,404,5],[406,0,406,8],[408,0,408,3],[409,0,409,5],[410,0,410,5],[685,1,685,5],[618,0,618,9],[620,0,620,9],[622,0,622,4],[623,0,623,4],[625,0,625,4],[624,8,624,9],[631,0,631,9],[663,1,663,8]]}
["OPIS TECHNICZNY"]
[]
["Węzeł cieplny dwufunkycjny centralnego ogrzewania oraz ciepłej wody użytkowej DSA WALL 2F-3 o kodzie 146B8774"]
[]
[]
["*Moduł przyłączeniowy nie jest ujęty w projekcie i obliczeniach węzła. Należy go wykonać zgodnie z wymaganiami lokalnego przedsiębiorstwa energetyki cieplnej"]
[]
[]
["Spis treści:"]
[{"$f":"A46","v":"1. Opis techniczny"}]
[{"$f":"A47","v":"1.1. Podstawa opracowania"}]
[{"$f":"A54","v":"1.2. Zakres opracowania"}]
[{"$f":"A59","v":"1.3. Opis ogólny węzła"}]
[{"$f":"A90","v":"2. Wyposażenie węzła cieplnego"}]
[{"$f":"A105","v":"2.1.1. Wymienniki ciepła"}]
[{"$f":"A123","v":"2.1.2. Pompa obiegowa c.o."}]
[{"$f":"A127","v":"2.1.3. Pompa cyrkulacyjna"}]
[{"$f":"A134","v":"2.1.4. Urządzenia automatycznej regulacji"}]
[{"$f":"A148","v":"2.1.5. Urządzenia filtrujące"}]
[{"$f":"A152","v":"2.1.6. Układ uzupełniania instalacji c.o."}]
[{"$f":"A159","v":"2.1.7. Naczynie wzbiorcze ciśnieniowe"}]
[{"$f":"A178","v":"2.1.8. Osprzęt (zawory zaporowe, bezpieczeństwa)"}]
[{"$f":"A190","v":"2.1.9. Połączenia rurowe"}]
[{"$f":"A195","v":"3. Założenia konstrukcyjne."}]
[{"$f":"A222","v":"4. Wymagania dotyczące miejsca zamontowania węzła (wg PN-99/B-02423)"}]
[{"$f":"A266","v":"5. Obliczenia hydrauliczne"}]
["6. Załączniki"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Dokumentacja, wykonana zgodnie z obowiązującymi wytycznymi i normami, została sprawdzona i uznana za sporządzoną prawidłowo. Może ona być skierowana do realizacji."]
[]
[]
[]
["1. Opis techniczny"]
["1.1. Podstawa opracowania"]
["• zlecenie inwestora,"]
["• wytyczne projektowania węzłów cieplnych,"]
["• uzgodnienia branżowe,"]
["• katalogi urządzeń i liczników ciepła,"]
["• obowiązujące normy i przepisy."]
[]
["1.2. Zakres opracowania"]
["          Przedmiotem opracowania jest projekt kompaktowego węzła cieplnego pracującego na potrzeby centralnego ogrzewania oraz podgrzewu ciepłej wody użytkowej.\nWęzeł będzie zasilany w czynnik grzewczy z zewnętrznej sieci wysokoparametrowej."]
[]
[]
[]
["1.3. Opis ogólny węzła"]
[" Węzeł projektuje się jako dwufunkcyjny centralnego ogrzewania i ciepłej wody użytkowej typu DSA WALL"]
[]
["Od storny pierwotnej węzeł cieplny zostanie połączony z miejską siecią cieplną, natomiast od strony wtórnej c.o. z instalacją centralnego ogrzewania, a od strony c.w.u. z zimną wodą i ciepłą wodą oraz cytkulacją.\nCiepło przekazywane będzie z sieci cieplnej do instalacji c.o. i c.w.u. za pośrednictwem wysokosprawnych płytowych wymienników ciepła.\nPrawidłowy obieg wody instalacyjnej c.o. będzie zapewniony poprzez pompę obiegową, zamontowaną na rurociągu zasilającym, natomiast przepływ ciepłej wody w przewodzie głównym i cyrkulacyjnym będzie wymuszany za pomocą pompy cyrkulacyjnej. \nPołączenie pośrednie instalacji c.o. z zewnętrzną siecią cieplną wymaga zastosowania naczyń ciśnieniowych, które przejmują zmiany objętości czynnika grzewczego przy wzroście temperatury oraz stabilizację ciśnienia statycznego. Instalacja c.o. i c.w.u. będzie zabezpieczona przed nadmiernym wzrostem ciśnienia za pomocą zaworów bezpieczeństwa, natomiast ubytki wody instalacyjnej będą uzupełniane wodą z powrotu sieciowego.\nProjektowany węzeł cieplny wyposażony będzie w układy kontrolno-pomiarowe, które będą spełniać następujące funkcje:"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["• automatyczna kontrola temperatury instalacji c.o. i c.w.u. będzie realizowana za pomocą elektronicznego regulatora pogodowego,"]
[]
["• pomiar temperatury i ciśnienia instalacyjnego zapewnią termomanometry."]
["Projektowany węzeł cieplny wyposażony będzie w skrzynkę bezpiecznikową z której zasialne będą urządzenia elektryczne - wg załączonego schematu"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["2. Wyposażenie węzła cieplnego"]
["          Zakładanym celem przy projektowaniu węzła cieplnego na potrzeby c.o. i c.w.u. jest uzyskanie komfortu cieplnego ogrzewanych pomieszczeń oraz ciepłej wody użytkowej. Aby to osiągnąć, węzeł powinien być wyposażony w następujące  urządzęnia:"]
[]
[]
["1. wymienniki ciepła c.o. i c.w.u.,"]
["2. pompę obiegową c.o. i cyrkulacyjną c.w.u.,"]
["3. urządzenia automatycznej regulacji,"]
["4. urządzenia filtrujące,"]
["5. układ uzupełniania instalacji c.o.,"]
["6. naczynie wzbiorcze ciśnieniowe,"]
["7. osprzęt (zawory zaporowe, bezpieczeństwa),"]
["8. urządzenia do kontroli i pomiarów,"]
["9. urządzenia elektryczne,"]
["10. wszelkie niezbędne połączenia rurowe."]
[]
["2.1.1. Wymienniki ciepła"]
["          Transformacja parametrów termodynamicznych w węźle następuje w wymiennikach płytowych typu Micro PlateTM firmy Danfoss.\nKonstrukcja wymienników tego typu pozwala na osiągnięcie bardziej efektywnego transferu ciepła, zmniejszenia oporów przepływu oraz wydłużenia żywotności produktu. Wymienniki te zapewniają wysokie schłodzenie wody sieciowej.\nWymienniki ciepła wykonane są ze stali konstrukcyjnej wysokiej jakości - jest to stal kwasoodporna typu AISI 316L.\nWymienniki posiadają podstawę umożliwiającą instalację na konstrukcji wsporczej węzła, dzięki czemu unika się występowania dodatkowych obciążeń pojawiąjących się po napełnieniu wymiennika medium i naprężenia nie są przenoszone na krócće.\nKlasa wymienników jest zgodna z PED, jest to klasyfikacja wymienników ciepła na kategorie wg Dyrektywy dot. Urządzeń Ciśnieniowych (PED) 97/23/EC."]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[{"$f":"\"W projektowanym węźle cieplnym na potrzeby centralnego ogrzewania dobrano wymiennik\nXB37L-1-10, który dla projektowych warunków generuje spadki ciśnienia po stronie sieciowej \"&I322&\"kPa i \"&I323&\"kPa po stronie instalacyjnej. Natomiast dla ciepłej wody użytkowej dobrano wymiennik\nXB37M-1-16, który dla projektowych warunków generuje spadki ciśnienia po stronie sieciowej \"&I337&\"kPa i \"&I338&\"kPa po stronie instalacyjnej.\"","v":"W projektowanym węźle cieplnym na potrzeby centralnego ogrzewania dobrano wymiennik\nXB37L-1-10, który dla projektowych warunków generuje spadki ciśnienia po stronie sieciowej 0kPa i 0kPa po stronie instalacyjnej. Natomiast dla ciepłej wody użytkowej dobrano wymiennik\nXB37M-1-16, który dla projektowych warunków generuje spadki ciśnienia po stronie sieciowej 0kPa i 0kPa po stronie instalacyjnej."}]
[]
[]
[]
[]
[]
["2.1.2. Pompa obiegowa c.o."]
[{"$f":"\"          Prawidłowy obieg wody instalacyjnej zapewnia elektroniczna pompa obiegowa c.o.\nAlpha 2L 25-60 produkowana przez firmę Grundfos, której punkt pracy wynosi \"&ROUND(I502,2)&\" m3/h i \"&ROUND(I509,2)&\" kPa.\"","v":{"$error":"#VALUE!"}}]
[]
[]
["2.1.3. Pompa cyrkulacyjna"]
[{"$f":"\"          Prawidłowy obieg ciepłej wody użytkowej zapewnia pompa cyrkulacyjna\nUPS 25-60N produkowana przez firmę Grundfos, której punkt pracy wynosi \"&ROUND(I634,2)&\" m3/h i \"&ROUND(I640,2)&\" kPa.\"","v":"          Prawidłowy obieg ciepłej wody użytkowej zapewnia pompa cyrkulacyjna\nUPS 25-60N produkowana przez firmę Grundfos, której punkt pracy wynosi 0 m3/h i 28 kPa."}]
[]
[]
[]
[]
[]
["2.1.4. Urządzenia automatycznej regulacji"]
["          Układ automatyki oparty jest na elektronicznym regulatorze temperatury ECL 310 z regulacją pogodową posiadającym możliwość ustawienia harmonogramu tygodniowego indywidualnie dla każdego dnia tygodnia i obiegu oraz plan świąteczny. W funkcji pogodowej regulacji temperatury mierzona jest temperatura zewnętrzna i odpowiednio do niej dostosowywana temperatura zasilania instalacji ogrzewania. Przed uruchomieniem węzła regulator należy sparametryzować według wytycznych użytkownika. W skład urządzeń automatycznej regulacji wchodzą:"]
[]
[]
[]
[]
[]
["• elektroniczny regulator temperatury c.o. i c.w.u. typu ECL 310 firmy Danfoss"]
["• zawór regulacyjny c.o. typu VS2 z siłownikiem AMV10 firmy Danfoss"]
["• zawór regulacyjny c.w.u. typu VM2 z siłownikiem AMV11 firmy Danfoss"]
["• czujnik temperatury instalacji c.o. typu ESM-11,"]
["• czujnik temperatury instalacji c.w.u. typu ESMU-100,"]
["• czujnik temperatury zewnętrznej typu ESMT,"]
[]
["2.1.5. Urządzenia filtrujące"]
["          W celu zabezpieczenia urządzeń przed zanieczyszczeniami mechanicznnymi zastosowano po stronie instalacyjnej c.o. i c.w.u. filtry siatkowe typu BVR-DZR firmy Danfoss."]
[]
[]
["2.1.6. Układ uzupełniania instalacji c.o."]
["          Projektowany węzeł cieplny zostanie wyposażony w system uzupełniania instalacji c.o. składający się z:"]
[]
["• zaworów odcinających,"]
["• wodomierza wody gorącej,"]
[{"$f":"IF(I273>=90,\"zaworu zwrotnego.\",\"• zaworu uzupełniania zładu.\")","v":"• zaworu uzupełniania zładu."}]
[]
["2.1.7. Naczynie wzbiorcze ciśnieniowe"]
[{"$f":"\"          W celu zabezpieczenia instalacji c.o. przed nadmiernym wzrostem ciśnienia na skutek powiększenia objętości nośnika ciepła przy zmianie temperatury zaprojektowano wg normy PN-B-02414:1999 ciśnieniowe naczynie przeponowe firmy Ferro typu CO18W \"","v":"          W celu zabezpieczenia instalacji c.o. przed nadmiernym wzrostem ciśnienia na skutek powiększenia objętości nośnika ciepła przy zmianie temperatury zaprojektowano wg normy PN-B-02414:1999 ciśnieniowe naczynie przeponowe firmy Ferro typu CO18W "}]
[]
[]
["Są to naczynia przeponowe typu zamkniętego. Wewnątrz znajduje się elastyczna przepona oddzielająca przestrzeń gazową od nośnika ciepła, która zabezpiecza zład przed napowietrzeniem. Głównym zadaniem naczyń wzbiorczych jest wyrównywanie wahań ciśnienia występującego przy zmianie temperatury czynnika. Projektowane naczynie wzbiorcze będzie zamontowane w pomieszczeniu węzła, co znacznie uprości jego obsługę eksploatacyjną."]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["2.1.8. Osprzęt (zawory zaporowe, bezpieczeństwa)"]
["          Węzeł cieplny wyposażony będzie w następującą armaturę odcinającą:"]
["• po stronie parametrów wysokich - zawory kulowe gwintowane"]
["• po stronie parametrów niskich c.o. i c.w.u. - zawory kulowe gwintowane."]
["Cały system c.o. wraz z urządzeniami współpracującymi (wymiennik, pompa, naczynie ciśnieniowe) jest zabezpieczony od wzrostu ciśnienia ponad wartość dopuszczalną za pomocą zaworów bezpieczeństwa typu Syr 1915 dobranych zgodnie z normą PN-B-02414:1999. Po stronie wody sieciowej nie jest wymagany zawór bezpieczeństwa, ponieważ wszystkie urządzenia w tym obiegu muszą wytrzymać ciśnienie robocze sieci, a cały system jest zabezpieczony w źródle ciepła."]
[]
[]
[]
[]
["Obieg c.w.u. Został zabezpieczony przed wzrostem ciśnienia ponad dopuszczalną wartość zaworem bezpieczeństwa typu Syr 2115 zgodnie z normą PN-76/B-02440"]
[]
[]
["2.1.9. Połączenia rurowe"]
["         Wszystkie instalacje po stronie wysokich parametrów oraz niskiej strony CO wykonane będą z rur ze stali St37-8 łączonych przez spawanie. Rurociągi po stronie CWU zostaną wykonane ze stali nierdzewnej AISI304."]
[]
[]
[]
["3. Założenia konstrukcyjne."]
["3.1.  Po wykonaniu montażu urządzeń, należy przeprowadzić próbę ciśnieniową, w celu wyeliminowania ewentualnych nieszczelności w całym układzie."]
[]
[]
["3.2. Wszystkie przewody przesyłowe i urządzenia zostaną zabezpieczone przed korozją za pomocą powłok ochronnych."]
[]
[]
["3.3. Wymienniki cieplne zostaną pokryte fabryczną izolacją cieplną, natomiast osprzęt i linie przesyłowe w granicach węzła cieplnego zostaną pokryte izolacją termiczną typu Steinonorm."]
[]
[]
["3.4. Projektowany węzeł cieplny zainstalowany będzie w przeznaczonym do tego celu pomieszczeniu. Jest to węzeł o konstrukcji przystosowanej do montażu naściennego lub stojącego. Niewielkie wymiary pozwalają na zastosowanie transportu ręcznego poprzez drzwi o wymiarach 0.8x2.0 metra."]
[]
[]
[]
["3.5. Włączenie węzła do pracy wymaga podłączenia zasilania i powrotu wody sieciowej, podłączenia zasilania i powrotu wody instalacyjnej centralnego ogrzewania oraz podłączenia zimnej wody użytkowej, ciepłej wody użytkowej i cyrkulacji, a także naczyń wzbiorczych przeponowych.\nAby zapewnić prawidłową pracę węzła należy, po uruchomieniu układu przeprowadzić regulację automatyki ciepłowniczej."]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["4. Wymagania dotyczące miejsca zamontowania węzła (wg PN-99/B-02423)"]
["         Pomieszczenie, w którym będzie podłączony węzeł cieplny musi spełniać określone wymagania oraz być wyposażone w instalacje umożliwiające spełnienie założonych funkcji węzła cieplnego:"]
[]
["• pomieszczenie węzła cieplnego powinno mieć oświetlenie elektryczne i dzienne,"]
["• drzwi stalowe zamontowane tak, aby otwierały się pod naciskiem od strony pomieszczenia węzła, zabezpieczone zamkiem patentowym,"]
[]
["• w pomieszczeniu węzła wykonać wpust podłogowy do studzienki schładzającej wg projektu wodno-kanalizacyjnego,"]
[]
["• posadzka pomieszczenia powinna być gładka, zabezpieczona przed poślizgiem, niepalna, wytrzymała na uderzenia mechaniczne i nagłe zmiany temperatury oraz prowadzona ze spadkiem nie mniejszym niż 1% w kierunku kratki ściekowej lub studzienki schładzającej,"]
[]
[]
["• wentylacja grawitacyjna nawiewna - kanał w kształcie litery \"Z\","]
["• kanał wentylacji wywiewnej grawitacyjnej,"]
["Pozostałe warunki wykonania i odbioru węzłów cieplnych określone są w normach:"]
["PN-64/B-10400 - Urządzenia centralnego ogrzewania w budownictwie powszechnym. Wymagania i badania techniczne przy odbiorze."]
[]
["PN-92/M-34031 - Rurociągi pary i wody gorącej. Wymagania i badania techniczne."]
["PN-B-02414:1999 - Zabezpieczenie instalacji ogrzewań wodnych systemu zamkniętego z naczyniami wzbiorczymi przeponowymi - wymagania."]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["5. Obliczenia hydrauliczne"]
[]
["Dane do obliczeń"]
[]
["1. Parametry temperaturowe sieci  ZIMA",null,null,null,null,null,"zasilanie","Tzsz",{"$f":"'Dane wejściowe'!C5","v":0},"°C"]
[null,null,null,null,null,null,"powrót","Tpsz",{"$f":"'Dane wejściowe'!C6","v":""},"°C"]
[]
["2. Parametry temperaturowe sieci  LATO",null,null,null,null,null,"zasilanie","Tzsl",{"$f":"'Dane wejściowe'!C13","v":0},"°C"]
[null,null,null,null,null,null,"powrót","Tpsl",{"$f":"'Dane wejściowe'!C14","v":0},"°C"]
[]
["4. Ciśnienie dyspozycyjne",null,null,null,null,null,null,"Pd",100,"kPa"]
[]
["6. Ciśnienie dopuszczalne wody sieciowej",null,null,null,null,null,null,"Pmax",1.6,"Mpa"]
[]
["7. Parametry temperaturowe instalacji C.O.",null,null,null,null,null,"zasilanie","Tzico",{"$f":"'Dane wejściowe'!C7","v":0},"°C"]
[null,null,null,null,null,null,"powrót","Tpico",{"$f":"'Dane wejściowe'!C8","v":""},"°C"]
[]
["8. Parametry temperaturowe instalacji C.W.U.",null,null,null,null,null,"zasilanie","Tzicw",{"$f":"'Dane wejściowe'!C15","v":60},"°C"]
[null,null,null,null,null,null,"powrót","Tpicw",{"$f":"'Dane wejściowe'!C16","v":5},"°C"]
[]
["9. Zapotrzebowanie ciepła C.O.",null,null,null,null,null,null,"Nco",{"$f":"Arkusz3!G15","v":0},"kW"]
[]
["10. Zapotrzebowanie ciepła C.W.U.",null,null,null,null,null,null,"Ncwu",{"$f":"Arkusz3!G16","v":0},"kW"]
[]
["11. Opory instalacji C.O.",null,null,null,null,null,null,"Hico",20,"kPa"]
[]
["12. Opory instalacji C.W.U.",null,null,null,null,null,null,"Hicw",25,"kPa"]
[]
["8. Ciśnienie dopuszczalne instalacji C.O.",null,null,null,null,null,null,"Pmaxco",2.5,"bar"]
[]
["9. Ciśnienie dopuszczalne instalacji C.W.U.",null,null,null,null,null,null,"Pmaxcw",10,"bar"]
[]
["10. Ciśnienie statyczne",null,null,null,null,null,null,"Ps",{"$f":"'Dane wejściowe'!C10/10","v":0},"bar"]
[]
["11. Pojemność instalacji C.O.",null,null,null,null,null,null,"Vico",{"$f":"I286*8/1000","v":0},"m3"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Dobór wymiennika C.O."]
[]
["Obliczeniowa moc cieplna",null,null,null,null,null,null,"Nco",{"$f":"I286","v":0},"kW"]
["Temperatury do doboru wymiennika"]
[null,null,null,null,null,null,null,"Tzsz",{"$f":"I270","v":0},"°C"]
[null,null,null,null,null,null,null,"Tpsz",{"$f":"I271","v":""},"°C"]
[null,null,null,null,null,null,null,"Tzico",{"$f":"I280","v":0},"°C"]
[null,null,null,null,null,null,null,"Tpico",{"$f":"I281","v":""},"°C"]
[]
["Dla powyższych parametrów dobrano wymiennik:",null,null,null,null,null,"Danfoss","XB37L-1-10"]
["Materiał płyt dobranego wymiennika",null,null,null,null,null,null,"EN1,4404(AISI316L)"]
["Spadek ciśnienia po stronie sieciowej ",null,null,null,null,null,null,"Hwsco",{"$f":"'Wymienniki CO'!AY3","v":0},"kPa"]
["Spadek ciśnienia po stronie instalacyjnej ",null,null,null,null,null,null,"Hwico",{"$f":"'Wymienniki CO'!AZ3","v":0},"kPa"]
[]
[]
["Dobór wymiennika C.W.U."]
[]
["Obliczeniowa moc cieplna",null,null,null,null,null,null,"Ncw",{"$f":"I288","v":0},"kW"]
["Temperatury do doboru wymiennika"]
[null,null,null,null,null,null,null,"Tzsl",{"$f":"I273","v":0},"°C"]
[null,null,null,null,null,null,null,"Tpsl",{"$f":"I274","v":0},"°C"]
[null,null,null,null,null,null,null,"Tzicw",{"$f":"I283","v":60},"°C"]
[null,null,null,null,null,null,null,"Tpicw",{"$f":"I284","v":5},"°C"]
[]
["Dla powyższych parametrów dobrano wymiennik:",null,null,null,null,null,"Danfoss","XB37M-1-16"]
["Materiał płyt dobranego wymiennika",null,null,null,null,null,null,"EN1,4404(AISI316L)"]
["Spadek ciśnienia po stronie sieciowej ",null,null,null,null,null,null,"Hwscw",{"$f":"'Wymienniki CWU'!AY3","v":0},"kPa"]
["Spadek ciśnienia po stronie instalacyjnej ",null,null,null,null,null,null,"Hwi",{"$f":"'Wymienniki CWU'!AZ3","v":0},"kPa"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Obliczenia przepływów"]
[]
["Moc cieplna C.O.",null,null,null,null,null,null,"Nco",{"$f":"I286","v":0},"kW"]
["Moc cieplna C.W.U.",null,null,null,null,null,null,"Ncwu",{"$f":"I288","v":0},"kW"]
[]
["Temperatury do obliczeń przepływów",null,null,null,null,null,null,"Tzsz",{"$f":"I270","v":0},"°C"]
[null,null,null,null,null,null,null,"Tpsz",{"$f":"I271","v":""},"°C"]
[null,null,null,null,null,null,null,"Tzico",{"$f":"I280","v":0},"°C"]
[null,null,null,null,null,null,null,"Tpico",{"$f":"I281","v":""},"°C"]
[]
[null,null,null,null,null,null,null,"Tzsl",{"$f":"I273","v":0},"°C"]
[null,null,null,null,null,null,null,"Tpsl",{"$f":"I274","v":0},"°C"]
[null,null,null,null,null,null,null,"Tzicw",{"$f":"I332","v":60},"°C"]
[null,null,null,null,null,null,null,"Tpicw",{"$f":"I333","v":5},"°C"]
[]
["Dla powyższych parametrów obliczono przepływy:"]
[]
["Przepływ czynnika sieciowego C.O.",null,null,null,null,null,null,"Gco",{"$f":"(I357*0.86)/(I360-I361)","v":{"$error":"#VALUE!"}},"mᵌ/h"]
["Przepływ czynnika sieciowego C.W.U. ",null,null,null,null,null,null,"Gcw",{"$f":"(I358*0.86)/(I365-I366)","v":{"$error":"#DIV/0!"}},"mᵌ/h"]
[]
[]
["Przepływ czynnika instalacyjnego C.O.",null,null,null,null,null,null,"Gico",{"$f":"(I357*0.86)/(I362-I363)","v":{"$error":"#VALUE!"}},"mᵌ/h"]
["Przepływ czynnika instalacyjnego C.W.U.",null,null,null,null,null,null,"Gicw",{"$f":"(I358*0.86)/(I367-I368)","v":0},"mᵌ/h"]
["Przepływ czynnika cyrkulacji C.W.U.",null,null,null,null,null,null,"Gicy",{"$f":"I377*0.3","v":0},"mᵌ/h"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Dobór średnic rurociągów"]
[]
["Dobór średnicy rurociągu sieciowego wymiennika C.O."]
[]
["Przepływ czynnika sieciowego ",null,null,null,null,null,null,"Gs",{"$f":"I372","v":{"$error":"#VALUE!"}},"mᵌ/h"]
["Dobrano średnicę rurociągu sieciowego:",null,null,null,null,null,null,"DN",20,"mm"]
["Prędkość przepływu czynnika przez rurociąg:",null,null,null,null,null,null,"Ws",{"$f":"I403/(3.14*(I404/1000)^2/4)/3600","v":{"$error":"#VALUE!"}},"m/s"]
[]
["Dobór średnicy rurociągu sieciowego wymiennika C.W.U."]
[]
["Przepływ czynnika sieciowego ",null,null,null,null,null,null,"Gs",{"$f":"I373","v":{"$error":"#DIV/0!"}},"mᵌ/h"]
["Dobrano średnicę rurociągu sieciowego:",null,null,null,null,null,null,"DN",20,"mm"]
["Prędkość przepływu czynnika przez rurociąg:",null,null,null,null,null,null,"Ws",{"$f":"I409/(3.14*(I410/1000)^2/4)/3600","v":{"$error":"#DIV/0!"}},"m/s"]
[]
["Dobór średnicy rurociągu instalacyjnego C.O."]
[]
["Przepływ czynnika instalacyjnego",null,null,null,null,null,null,"Gico",{"$f":"I376","v":{"$error":"#VALUE!"}},"mᵌ/h"]
["Dobrano średnicę rurociągu instalacyjnego:",null,null,null,null,null,null,"DN",25,"mm"]
["Prędkość przepływu czynnika przez rurociąg:",null,null,null,null,null,null,"Wico",{"$f":"I415/(3.14*(I416/1000)^2/4)/3600","v":{"$error":"#VALUE!"}},"m/s"]
[]
["Dobór średnicy rurociągu instalacyjnego C.W.U."]
[]
["Przepływ czynnika instalacyjnego",null,null,null,null,null,null,"Gicw",{"$f":"I377","v":0},"mᵌ/h"]
["Dobrano średnicę rurociągu instalacyjnego:",null,null,null,null,null,null,"DN",20,"mm"]
["Prędkość przepływu czynnika przez rurociąg:",null,null,null,null,null,null,"Wicw",{"$f":"I421/(3.14*(I422/1000)^2/4)/3600","v":0},"m/s"]
[]
["Przepływ czynnika cyrkulacji",null,null,null,null,null,null,"Gicwc",{"$f":"I378","v":0},"mᵌ/h"]
["Dobrano średnicę rurociągu cyrkulacji:",null,null,null,null,null,null,"DN",15,"mm"]
["Prędkość przepływu czynnika przez rurociąg:",null,null,null,null,null,null,"Wicwc",{"$f":"I425/(3.14*(I426/1000)^2/4)/3600","v":0},"m/s"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Dobór zaworu regulacyjnego C.O."]
[]
["Przepływ wody sieciowej przez zawór",null,null,null,null,null,null,"Gs",{"$f":"I372","v":{"$error":"#VALUE!"}},"mᵌ/h"]
[]
["Dobrano zawór VS2 produkcji Danfoss"]
[]
["Kvs zaworu ",null,null,null,null,null,null,"Kvs",1.6,"mᵌ/h"]
["Średnica nominalna",null,null,null,null,null,null,"DN",15,"mm"]
["Oopór zaworu całkowicie otwartego",null,null,null,null,null,null,"Hzco",{"$f":"((I445/I449)^2)*100","v":{"$error":"#VALUE!"}},"kPa"]
["Prędkość przepływu na wylocie zaworu",null,null,null,null,null,null,"Wzco",{"$f":"I445/(3.14*(I450/1000)^2/4)/3600","v":{"$error":"#VALUE!"}},"mᵌ/h"]
["Autorytet zaworu regulacyjnego",null,null,null,null,null,null,null,{"$f":"I451/(I451+I322+2)","v":{"$error":"#VALUE!"}}]
[]
["Dobór zaworu regulacyjnego C.W.U."]
[]
["Przepływ wody sieciowej przez zawór",null,null,null,null,null,null,"Gs",{"$f":"I373","v":{"$error":"#DIV/0!"}},"mᵌ/h"]
[]
["Dobrano zawór VM2 produkcji Danfoss"]
[]
["Kvs zaworu ",null,null,null,null,null,null,"Kvs",2.5,"mᵌ/h"]
["Średnica nominalna",null,null,null,null,null,null,"DN",15,"mm"]
["Opór zaworu całkowicie otwartego",null,null,null,null,null,null,"Hzcw",{"$f":"((I457/I461)^2)*100","v":{"$error":"#DIV/0!"}},"kPa"]
["Prędkość przepływu na wylocie zaworu",null,null,null,null,null,null,"Wzcw",{"$f":"I457/(3.14*(I462/1000)^2/4)/3600","v":{"$error":"#DIV/0!"}},"mᵌ/h"]
["Autorytet zaworu regulacyjnego",null,null,null,null,null,null,null,{"$f":"I463/(I463+I337+2)","v":{"$error":"#DIV/0!"}}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Dobór komponentów modułu C.O."]
[]
["Dobór urządzeń filtrujących"]
[]
["Przepływ wody instalacyjnej przez filtr",null,null,null,null,null,null,"Gi",{"$f":"I376","v":{"$error":"#VALUE!"}},"mᵌ/h"]
[]
["Dobrano filtr (z siatką 280 oczek/cm2) firmy Danfoss",null,null,null,null,null,null,"typu","BVR-DZR"]
[]
["średnica",null,null,null,null,null,null,"DN",25,"mm"]
["współczynnik przepływu",null,null,null,null,null,null,"Kvs",10,"mᵌ/h"]
["ciśnienie",null,null,null,null,null,null,"PN",1.6,"MPa"]
["strata ciśnienia",null,null,null,null,null,null,"Hfco",{"$f":"(I491/I496)^2*100","v":{"$error":"#VALUE!"}},"kPa"]
[]
["Dobór pompy obiegowej"]
[]
["Przepływ wody instalacyjnej przez pompę",null,null,null,null,null,null,"Gi",{"$f":"I376","v":{"$error":"#VALUE!"}},"mᵌ/h"]
[]
["opór instalacji C.O.",null,null,null,null,null,null,"Hi",{"$f":"I290","v":20},"kPa"]
["opór wymiennika C.O. strona instalacyjna",null,null,null,null,null,null,"Hwi",{"$f":"I323","v":0},"kPa"]
["opór urządzeń filtrujących",null,null,null,null,null,null,"Hfco",{"$f":"I498","v":{"$error":"#VALUE!"}},"kPa"]
["opory miejscowe i liniowe",null,null,null,null,null,null,null,5,"kPa"]
[null,null,null,null,null,null,null,null,{"$f":"SUM(I504:I506)","v":{"$error":"#VALUE!"}}]
["wymagana wysokość podnoszenia",null,null,null,null,null,null,null,{"$f":"SUM(I504:I507)","v":{"$error":"#VALUE!"}},"kPa"]
[]
["Dobrano pompę Alpha 2L 25-60 firmy Grundfos"]
["Zasilanie",null,"A/V","0,32 / 1*230"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Dobór przeponowego naczynia wzbiorczego"]
["Obliczenia przeprowadzono zgodnie z normą PN-B-02414:1999"]
[]
["Dobrano naczynie wzbiorcze:"]
[null,"Typ",null,null,null,null,null,null,{"$f":"'PN-NWP'!H7","v":{"$error":"#N/A"}}]
[null,"Ilość naczyń",null,null,null,null,null,null,{"$f":"'PN-NWP'!H8","v":1},"szt."]
[null,"Pojemność naczynia                                     ",null,null,null,null,null,null,{"$f":"'PN-NWP'!H9","v":{"$error":"#N/A"}},"l"]
[null,"Wysokość",null,null,null,null,null,null,{"$f":"'PN-NWP'!H10","v":{"$error":"#N/A"}},"mm"]
[null,"Średnica",null,null,null,null,null,null,{"$f":"'PN-NWP'!H11","v":{"$error":"#N/A"}},"mm"]
[null,"Średnica przyłącza",null,null,null,null,null,null,{"$f":"'PN-NWP'!H12","v":{"$error":"#N/A"}},"mm"]
[null,"Ciśnienie wstepne",null,null,null,null,null,null,{"$f":"'PN-NWP'!H13","v":0.2},"bar"]
[null,"Producent",null,null,null,null,null,null,{"$f":"'PN-NWP'!H14","v":{"$error":"#N/A"}}]
[]
["Założenia:"]
[null,"Producent ",null,null,null,null,null,null,{"$f":"'PN-NWP'!H18","v":"FERRO"}]
[null,"Pojemność instalacji",null,null,null,null,null,"V",{"$f":"'PN-NWP'!H19","v":0},"m3"]
[null,"Maksymalne obliczeniowe ciśnienie w naczyniu",null,null,null,null,null,"pmax",{"$f":"'PN-NWP'!H20","v":2.5},"bar"]
[null,"Ciśnienie statyczne w naczyniu",null,null,null,null,null,"pst",{"$f":"'PN-NWP'!H21","v":0},"bar"]
[null,"Obliczeniowa temperatura na zasilaniu instalacji",null,null,null,null,null,"tz",{"$f":"'PN-NWP'!H22","v":0},"oC"]
[null,"Przyrost objętości wody instalacyjnej",null,null,null,null,null,"Dn",{"$f":"'PN-NWP'!H23","v":{"$error":"#N/A"}},"l/kg"]
[null,"Gęstość wody instalacyjnej przy temp. T1=10oC",null,null,null,null,null,"r1",{"$f":"'PN-NWP'!H24","v":999.7},"kg/m3"]
[null,"Ilość naczyń",null,null,null,null,null,"n",{"$f":"'PN-NWP'!H25","v":1}]
[]
[null,"Pojemność użytkowa naczynia Vu:"]
[]
[null,null,null,"Vu = V x r1 x Dn / n"]
[]
[null,null,null,"Vu =",{"$f":"I546*I551*I550/I536","v":{"$error":"#N/A"}},"dm3"]
[]
[null,"Ciśnienie wstępne w przestrzeni gazowej"]
[]
[null,null,null,"p=",{"$f":"I548+0.2","v":0.2},"bar"]
[]
[null,"Minimalna pojemność całkowita naczynia"]
[]
[]
[]
[]
[]
[null,null,null,"Vn=",{"$f":"E558*(I547+1)/(I547-E562)","v":{"$error":"#N/A"}},"dm3"]
[]
[]
[]
[]
["Dobór zaworu bezpieczeństwa dla obiegu c.o."]
["Obliczenia przeprowadzono zgodnie z p. 2.2.2. normy PN-B-02414:1999"]
[null,null,null,null," "]
["Dobrano zawór bezpieczeństwa:"]
[null,"Typ",null,null,null,null,null,null,{"$f":"'PN-C.O.'!H7","v":1915}]
[null,"Średnica nominalna                                                                       ",null,null,null,null,null,null,{"$f":"'PN-C.O.'!H8","v":"DN 25"},"mm"]
[null,"Ilość zaworów",null,null,null,null,null,null,{"$f":"'PN-C.O.'!H9","v":{"$error":"#N/A"}},"szt."]
[null,"Min. średnica wewnętrzna",null,null,null,null,null,"d0",{"$f":"'PN-C.O.'!H10","v":20},"mm"]
[null,"Ciśnienie początku otwarcia",null,null,null,null,null,"p0",{"$f":"'PN-C.O.'!H11","v":2.5},"bar"]
[null,"Wsp. wypływu dla cieczy",null,null,null,null,null,"acrz",{"$f":"'PN-C.O.'!H12","v":0.41}]
[null,"Producent",null,null,null,null,null,null,{"$f":"'PN-C.O.'!H13","v":"HUSTY SYR"}]
[]
["Założenia:"]
[null,"Producent ",null,null,null,null,null,null,{"$f":"'PN-C.O.'!H16","v":"HUSTY SYR"}]
[null,"Wstępnie zakładana średnica zaworu bezpieczeństwa",null,null,null,null,null,null,{"$f":"'PN-C.O.'!H17","v":25},"mm"]
[null,"Ciśnienie nastawy zaworu bezpieczeństwa",null,null,null,null,null,"p1",{"$f":"'PN-C.O.'!H18","v":2.5},"bar"]
[null,"Ciśnienie nominalne sieci ciepłowniczej",null,null,null,null,null,"p2",{"$f":"'PN-C.O.'!H19","v":16},"bar"]
[null,"Obliczeniowa temperatura wody sieciowej",null,null,null,null,null,null,{"$f":"'PN-C.O.'!H20","v":0},"0C"]
[null,"Gęstość wody sieciowej przy jej obliczeniowej temp.",null,null,null,null,null,"r",{"$f":"'PN-C.O.'!H21","v":{"$error":"#N/A"}},"kg/m3"]
[null,"Dopuszczalny wsp. wypływu zaworu dla cieczy",null,null,null,null,null,"ac=0,9*acrz",{"$f":"'PN-C.O.'!H22","v":0.36899999999999999}]
[]
[null,"Wymagana masowa przepustowość zaworu bezpieczeństwa [kg/s]",null,null,null,null,null,null," "]
[]
[]
[null,null,"b = 1","gdy    p2 - p1 ≤ 5 bar"]
[null,null,"b = 2","gdy    p2 - p1 > 5 bar"]
[]
[null,null,"p2 - p1=",{"$f":"CONCATENATE(L785,\" bar\")","v":" bar"},"b =",{"$f":"IF(L785>5,2,1)","v":1}]
[]
[null,null,"A =",{"$f":"'PN-C.O.'!D33","v":1.5999999999999999E-5},"wg. karty katalogowej",null,null,{"$f":"'PN-C.O.'!H33:I33","v":"XB37L"}]
[null,null,"M = ",{"$f":"'PN-C.O.'!D34","v":{"$error":"#N/A"}},"kg/s"]
[null,"Minimalna średnica wewnętrzna pojedynczego zaworu bezpieczeństwa:"]
[]
[]
[null,null,null,null,null,{"$f":"54*SQRT((D605/I581/(I594*SQRT(I590*I593))))","v":{"$error":"#N/A"}},"mm <  do   =",{"$f":"I582","v":20},"mm"]
[]
[]
[null,"Warunek: do > domin jest spełniony."]
[]
[]
[]
[null,"Dobrany zawór bezpieczeństwa spełnia wymagania normy PN-B-02414"]
[]
[]
["Dobór komponentów modułu C.W.U."]
[]
["Dobór urządzeń filtrujących Z.W."]
[]
["Przepływ wody instalacyjnej przez filtr ZW",null,null,null,null,null,null,"Gi",{"$f":"I377","v":0},"mᵌ/h"]
[]
["Dobrano filtr (z siatką 280 oczek/cm2) firmy Danfoss",null,null,null,null,null,null,"typu","FVR-DZR"]
[]
["średnica",null,null,null,null,null,null,"DN",20,"mm"]
["współczynnik przepływu",null,null,null,null,null,null,"Kvs",8,"mᵌ/h"]
["ciśnienie",null,null,null,null,null,null,"PN",1.6,"MPa"]
["strata ciśnienia",null,null,null,null,null,null,"Hfzw",{"$f":"(I623/I628)^2*100","v":0},"kPa"]
[]
["Dobór pompy cyrkulacyjnej"]
[]
["Przepływ wody instalacyjnej przez pompę",null,null,null,null,null,null,"Gi",{"$f":"I378","v":0},"mᵌ/h"]
[]
["opór instalacji C.W.U",null,null,null,null,null,null,"Hi",{"$f":"I292","v":25},"kPa"]
["opór wymiennika C.W.U. strona instalacyjna dla przepływu cyrkulacji",null,null,null,null,null,null,"Hwcy",{"$f":"I338*0.3","v":0},"kPa"]
["opory miejscowe i liniowe",null,null,null,null,null,null,null,3,"kPa"]
[null,null,null,null,null,null,null,null,{"$f":"SUM(I636:I637)","v":25}]
["wymagana wysokość podnoszenia",null,null,null,null,null,null,null,{"$f":"SUM(I636:I638)","v":28},"kPa"]
[]
["Dobrano pompę UPS 25-60N firmy Grundfos"]
["Zasilanie",null,"A/V","0,3 / 1*230"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"Dobór zaworu bezpieczeństwa dla obiegu c.w.u"]
[null,"Obliczenia przeprowadzono zgodnie z p.. 3.2.5.2. normy PN-76/B-02440"]
[]
["Dobrano zawór bezpieczeństwa:"]
[null,"Typ",null,null,null,null,null,null,{"$f":"'PN-C.W.U.'!H7","v":2115}]
[null,"Średnica nominalna                                                                      ",null,null,null,null,null,null,{"$f":"'PN-C.W.U.'!H8","v":"DN 20"},"mm"]
[null,"Ilość zaworów",null,null,null,null,null,null,{"$f":"'PN-C.W.U.'!H9","v":1},"szt."]
[null,"Min. średnica wewnętrzna",null,null,null,null,null,"d0",{"$f":"'PN-C.W.U.'!H10","v":14},"mm"]
[null,"Ciśnienie początku otwarcia",null,null,null,null,null,"p0",{"$f":"'PN-C.W.U.'!H11","v":6},"bar"]
[null,"Wsp. wypływu dla gazu dla dobranych zaworów",null,null,null,null,null,"a",{"$f":"'PN-C.W.U.'!H12","v":0.55000000000000004}]
[null,"ac dla dobranego zaworu",null,null,null,null,null,"ac=0,35*a",{"$f":"'PN-C.W.U.'!H13","v":0.1925}]
[null,"Wsp. wypływu wody grzejnej ",null,null,null,null,null,"ac1",{"$f":"'PN-C.W.U.'!H14","v":1}]
[null,"Producent",null,null,null,null,null,null,{"$f":"'PN-C.W.U.'!H15","v":"HUSTY SYR"}]
[]
["Założenia:"]
[null,"Producent ",null,null,null,null,null,null,{"$f":"'PN-C.W.U.'!H18","v":"HUSTY SYR"}]
[null,"Wstępnie zakładana średnica zaworu bezpieczeństwa",null,null,null,null,null,null,{"$f":"'PN-C.W.U.'!H19","v":20},"mm"]
[null,"Ciśnienie dopuszczalne instalacji cwu",null,null,null,null,null,"p1",{"$f":"'PN-C.W.U.'!H20","v":6},"bar"]
[null,"Ciśnienie na wylocie zaworu bezpieczeństwa",null,null,null,null,null,"p2",{"$f":"'PN-C.W.U.'!H21","v":0},"bar"]
[null,"Ciśnienie czynnika grzejnego",null,null,null,null,null,"p3",{"$f":"'PN-C.W.U.'!H22","v":16},"bar"]
[null,"Najniższa temperatura wody grzejnej na zasilaniu",null,null,null,null,null,"T1",{"$f":"'PN-C.W.U.'!H23","v":0},"0C"]
[null,"Ciężar objętościowy wody przy jej obliczeniowej temperaturze",null,null,null,null,null,"g1",{"$f":"'PN-C.W.U.'!H24","v":977.81},"kg/m3"]
[]
[null,"Wymagana przepustowość zaworu bezp."]
[]
[]
[null,null,"b = 1","gdy p3 - p1 ≤ 5 kG/cm2"]
[null,null,"b = 2","gdy p3 - p1 > 5 kG/cm2"]
[]
[null,null,"p3 - p1=",{"$f":"CONCATENATE(L692,\" bar\")","v":" bar"},"b =",{"$f":"IF(L692>4.9,2,1)","v":1}]
[null,null,"F =",{"$f":"'PN-C.W.U.'!D34","v":11},"wg. karty katalogowej",null,null,"XB 37M"]
[null,null,"G = ",{"$f":"'PN-C.W.U.'!D36","v":3494.0893344010988},"kg/h"]
[]
[null,"Min. średnica wewn. dla pojedynczego zaworu bezp :"]
[]
[null,null,null,null,null,{"$f":"SQRT(((4*D694/I669)/(3.14*1.59*I673*SQRT((1.1*I680-I681)/0.98*I684))))","v":13.386750255700287},"mm < do =",{"$f":"I670","v":14},"mm"]
[]
[]
[null,"Warunek: do > domin jest spełniony."]
[]
[]
[null,"Dobrany zawór bezpieczeństwa spełnia wymagania normy PN-76/B-02440"]
[]
[]
["Karta doboru węzła"]
["Wymiennik ciepła",null,null,null,"Jednostka","Ogrzewanie",null,"Woda użytkowa"]
["Producent",null,null,null,null,"Danfoss",null,"Danfoss"]
["Typ",null,null,null,null,{"$f":"H320","v":"XB37L-1-10"},null,{"$f":"H335","v":"XB37M-1-16"}]
["Kategoria-PED",null,null,null,null,"Class I",null,"Class I"]
["Moc",null,null,null,"kW",{"$f":"I313","v":0},null,{"$f":"I328","v":0}]
["",null,null,null,null,"Pierwotny","Wtórny","Pierwotny","Wtórny"]
["Ogólne parametry projektowe węzła cieplnego"]
["Maks. temp. (°C) / Maks. Ciśnienie (bar)",null,null,null,null,"130,0 / 14,3","90,0 / 5,7","130,0 / 14,3","60,0 / 10,0"]
["Natężenie przepływu",null,null,null,"m3/h",{"$f":"I372","v":{"$error":"#VALUE!"}},{"$f":"I376","v":{"$error":"#VALUE!"}},{"$f":"I373","v":{"$error":"#DIV/0!"}},{"$f":"I377","v":0}]
["Temperatura",null,null,null,"°C / °C",{"$f":"I270&\" / \"&I271","v":"0 / "},{"$f":"I362&\" / \"&I363","v":"0 / "},{"$f":"I365&\" / \" &I366","v":"0 / 0"},{"$f":"I367&\" / \" &I368","v":"60 / 5"}]
["Spadek ciśnienia",null,null,null,"kPa",{"$f":"I322","v":0},{"$f":"I323","v":0},{"$f":"I337","v":0},{"$f":"I338","v":0}]
["Ciśnienie nominalne",null,null,null,"bar","16","6","16","10"]
["Materiał płyt",null,null,null,null,"EN1,4404(AISI316L)",null,"EN1,4404(AISI316L)"]
["Czynnik",null,null,null,null,"Woda","Woda","Woda","Woda"]
["",null,null,null,null," "," "," "," "]
["",null,null,null,"Ogrzewanie","Pierwotny","Wtórny","Pierwotny","Wtórny"]
["Średnice przyłączy (DN)",null,null,null,25,20,25,20,"20 / 15"]
["Zawory regulacyjne"]
["Producent",null,null,null,null,"Danfoss",null,"Danfoss"]
["Typ",null,null,null,null,"VS 2",null,"VM 2"]
["Natężenie przepływu",null,null,null,"m3/h",{"$f":"F716","v":{"$error":"#VALUE!"}},null,{"$f":"H716","v":{"$error":"#DIV/0!"}}]
["Spadek ciśnienia",null,null,null,"kPa",{"$f":"I451","v":{"$error":"#VALUE!"}},null,{"$f":"I463","v":{"$error":"#DIV/0!"}}]
["Wartość kvs",null,null,null,"DN / kvs","15/1,6",null,"15/2,5"]
["Regulator",null,null,null,"Danfoss","ECL Comfort 310, 230V (A266)"]
["Pompy"]
["Producent",null,null,null,null,"Grundfos",null,"Grundfos"]
["Typ",null,null,null,null,"Alpha 2L 25-60",null,"UPS 25-60 N 180"]
["Natężenie przepływu",null,null,null,"m3/h",{"$f":"G716","v":{"$error":"#VALUE!"}},null,{"$f":"I378","v":0}]
["Wysokość podnoszenia",null,null,null,"kPa",{"$f":"I509","v":{"$error":"#VALUE!"}},null,{"$f":"I640","v":28}]
["Zasilanie",null,null,null,"A / V","0,32 / 1*230",null,"0,3 / 1*230"]
["Dodatkowe informacje"]
["Dane obliczeniowe",null,"Temperatury",null,"°C / °C",{"$f":"F717","v":"0 / "},{"$f":"G717","v":"0 / "},{"$f":"H717","v":"0 / 0"},{"$f":"I717","v":"60 / 5"}]
["Dane obliczeniowe",null,"Dopuszczalne dp",null,"kPa","20","20","20","20"]
["Całkowity spadek ciś. po str. pierw.",null,null,null,"kPa",{"$f":"MAX(SUM(F718+F729+2),SUM(H718+H729+2))","v":{"$error":"#VALUE!"}}]
["Dopuszczalny spadek ciś. dla węzła",null,null,null,"kPa",{"$f":"I276","v":100}]

{"sheet":"Dane wejściowe","index":1,"n_rows":35,"n_cols":4,"rows_kept":35,"cut":false,"hidden":false,"merged":[[34,0,35,5]]}
[]
[null,"Dane do obliczeń (należy wypełnić białe pola)"]
[]
[null,"Wybierz program temperatur C.O."]
[null,"Temperatura zasilania wody sieciowej (z warunków uzyskanych od dostawcy ciepła systemowego)",null,"°C"]
[null,"Temperatura powrotu wody sieciowej",{"$f":"IF(C7>=70,C8+5,\"\")","v":""},"°C"]
[null,"Temperatura zasilania instalacji c.o.",null,"°C"]
[null,"Temperatura powrotu instalacji c.o.",{"$f":"IF(C7<50,\"\",C7-20)","v":""},"°C"]
[]
[null,"Wysokość budynku",null,"m"]
[]
[null,"Wybierz program temperatur C.W.U."]
[null,"Temperatura zasilania wody sieciowej (z warunków uzyskanych od dostawcy ciepła systemowego)",null,"°C"]
[null,"Temperatura powrotu wody sieciowej (z warunków uzyskanych od dostawcy ciepła systemowego)",null,"°C"]
[null,"Temperatura zasilania c.w.u.",60,"°C"]
[null,"Temperatura wody zimnej",5,"°C"]
[]
[null,"Moc C.O. (1do30kW) (jeżeli nie znasz, przejdź do tabeli poniżej)",null,"kW"]
[null,"Moc C.W.U.(1do60kW) (jeżeli nie znasz, przejdź do tabeli poniżej)",null,"kW"]
[]
[]
[null,"Jeżeli nie znasz mocy podaj:"]
[null,"Powierzchnia ogrzewanych pomieszczeń",null,"m2"]
[null,"Wysokość ogrzewanych pomieszczeń",null,"m"]
[null,"Izolacja budynku"]
[null,"Na podstawie powyższych danych obliczono",{"$f":"Arkusz3!D20","v":0},"kW"]
[]
[null,"Ilość użytkowników C.W.U.",null,"osoby"]
[null,"Na podstawie powyższych danych obliczono",{"$f":"Arkusz3!D21","v":0},"kW"]
[]
[]
[]
[]
[]
[{"$f":"IF(Arkusz3!G23=0,\"\",\"Dla podanych danych należy zakupić dodatkowe naczynie o pojemności \"&Arkusz3!G23&\" litrów lub należy wymienić istniejące na zgodne z kartą doboru\")","v":{"$error":"#N/A"}}]

{"sheet":"Wymienniki CWU","index":2,"n_rows":484,"n_cols":58,"rows_kept":484,"cut":false,"hidden":true,"merged":[]}
["Data","2017-09-09T11:22:52"]
["aplikacja","X Danfoss-XB",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"spadek po str siec","spadek po str inst"]
["Tryb","Sprawdzenie",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SUM(AY5:AY484)","v":0},0]
["isROT","Standardowy","Dozw. komb. płyt M Mieszanie płyt","Współprądowy","Równoległy","J.m.","Ilość stopni","Wymiennik ciepła","Typ płyty","Ilość kanałów kanału nr 1 Strona1","Ilość kanałów kanału nr 1 Strona2","Ilość kanałów kanału nr 2 Strona1","Ilość kanałów kanału nr 2 Strona2","Moc\n[kW]","Zapas powierzchni\n[%]","Czynnik Strona 1","Gaz1","Stężenie1\n[%]","Abs. Pressure1\n[bar]","Czynnik Strona 2","Gaz2","Stężenie2\n[%]","Abs. Pressure2\n[bar]","Temperatura na wlocie1\n[°C]","Temperatura na wylocie1\n[°C]","Masowe Natężenie przepływu1\n[kg/h]","Objętościowe Natężenie przepływu1\n[L/min]","Maks. spadek ciśnienia1\n[kPa]","Temperatura na wlocie2\n[°C]","Temperatura na wylocie2\n[°C]","Masowe Natężenie przepływu2\n[kg/h]","Objętościowe Natężenie przepływu2\n[L/min]","Maks. spadek ciśnienia2\n[kPa]","Masowe Natężenie przepływu Szer.-Równ.\n[kg/h]","Objętościowe Natężenie przepływu Szer.-Równ.\n[L/min]","Maks. spadek ciśnienia Szer.-Równ.\n[kPa]","FrameExtension(%)","Wymiennik ciepła","Grupowanie","Termin dostawy","PED","Zapas powierzchni\n[%]","Całkowita pow.\n[m^2]","HTC(Dostępny / Wymagany)\n[W/m^2-K]","LMTD\n[K]","NTU-1","NTU-2","Całkowity spadek ciśnienia-1\n[kPa]","Całkowity spadek ciśnienia-2\n[kPa]",null,{"$f":"ROUNDUP(Arkusz3!G16,0)","v":0},{"$f":"'Dane wejściowe'!C13","v":0},{"$f":"'Dane wejściowe'!C14","v":0}]
[0,0,0,0,1,1,1,"XB37","M",7,8,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","373,4","0,78","331,7/70,1","18,20","1,92","3,03","0,02","0,01",{"$f":"AND(N5=$AY$4,X5=$AZ$4,Y5=$BA$4)","v":false},{"$f":"AX5*AV5","v":0},{"$f":"AX5*AW5","v":0}]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","287,4","0,78","542,9/140,1","18,20","1,92","3,03","0,06","0,03",{"$f":"AND(N6=$AY$4,X6=$AZ$4,Y6=$BA$4)","v":false},{"$f":"AX6*AV6","v":0},{"$f":"AX6*AW6","v":0},null,null,1,3,{"$f":"AND('Dane wejściowe'!$C$28>=BC6,'Dane wejściowe'!$C$28<BC7)","v":false},{"$f":"BD6*BE6","v":0}]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","244,6","0,78","724,4/210,2","18,20","1,92","3,03","0,11","0,05",false,0,0,null,null,2,3.5,{"$f":"AND('Dane wejściowe'!$C$28>=BC7,'Dane wejściowe'!$C$28<BC8)","v":false},{"$f":"BD7*BE7","v":0}]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","217,2","0,78","888,8/280,3","18,20","1,92","3,03","0,18","0,08",false,0,0,null,null,3,4,{"$f":"AND('Dane wejściowe'!$C$28>=BC8,'Dane wejściowe'!$C$28<BC9)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","197,3","0,78","1041,7/350,3","18,20","1,92","3,03","0,26","0,11",false,0,0,null,null,4,4.5,{"$f":"AND('Dane wejściowe'!$C$28>=BC9,'Dane wejściowe'!$C$28<BC10)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","182,1","0,78","1185,8/420,4","18,20","1,92","3,03","0,36","0,15",false,0,0,null,null,5,5,{"$f":"AND('Dane wejściowe'!$C$28>=BC10,'Dane wejściowe'!$C$28<BC11)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","169,8","0,78","1323,0/490,5","18,20","1,92","3,03","0,46","0,20",false,0,0,null,null,6,5.5,{"$f":"AND('Dane wejściowe'!$C$28>=BC11,'Dane wejściowe'!$C$28<BC12)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","159,5","0,78","1454,6/560,5","18,20","1,92","3,03","0,57","0,25",false,0,0,null,null,7,6,{"$f":"AND('Dane wejściowe'!$C$28>=BC12,'Dane wejściowe'!$C$28<BC13)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","150,8","0,78","1581,4/630,6","18,20","1,92","3,03","0,70","0,30",false,0,0,null,null,8,6.5,{"$f":"AND('Dane wejściowe'!$C$28>=BC13,'Dane wejściowe'!$C$28<BC14)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","143,2","0,78","1704,1/700,6","18,20","1,92","3,03","0,83","0,36",false,0,0,null,null,9,7,{"$f":"AND('Dane wejściowe'!$C$28>=BC14,'Dane wejściowe'!$C$28<BC15)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","136,6","0,78","1823,3/770,7","18,20","1,92","3,03","0,97","0,42",false,0,0,null,null,10,7.5,{"$f":"AND('Dane wejściowe'!$C$28>=BC15,'Dane wejściowe'!$C$28<BC16)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","130,6","0,78","1939,2/840,8","18,20","1,92","3,03","1,12","0,48",false,0,0,null,null,12,8,{"$f":"AND('Dane wejściowe'!$C$28>=BC16,'Dane wejściowe'!$C$28<BC17)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","125,3","0,78","2052,3/910,8","18,20","1,92","3,03","1,27","0,55",false,0,0,null,null,15,9,{"$f":"AND('Dane wejściowe'!$C$28>=BC17,'Dane wejściowe'!$C$28<BC18)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","120,5","0,78","2162,8/980,9","18,20","1,92","3,03","1,44","0,62",false,0,0,null,null,20,10,{"$f":"AND('Dane wejściowe'!$C$28>=BC18,'Dane wejściowe'!$C$28<BC19)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","116,1","0,78","2271,0/1051,0","18,20","1,92","3,03","1,61","0,69",false,0,0,null,null,30,12,{"$f":"AND('Dane wejściowe'!$C$28>=BC19,'Dane wejściowe'!$C$28<BC20)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","112,0","0,78","2377,1/1121,0","18,20","1,92","3,03","1,79","0,77",false,0,0,null,null,40,14,{"$f":"AND('Dane wejściowe'!$C$28>=BC20,'Dane wejściowe'!$C$28<BC21)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","108,3","0,78","2481,1/1191,1","18,20","1,92","3,03","1,98","0,85",false,0,0,null,null,50,16,{"$f":"AND('Dane wejściowe'!$C$28>=BC21,'Dane wejściowe'!$C$28<BC22)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","104,8","0,78","2583,3/1261,2","18,20","1,92","3,03","2,18","0,94",false,0,0,null,null,65,17,{"$f":"AND('Dane wejściowe'!$C$28>=BC22,'Dane wejściowe'!$C$28<BC23)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","101,6","0,78","2683,8/1331,2","18,20","1,92","3,03","2,38","1,03",false,0,0,null,null,100,18,{"$f":"AND('Dane wejściowe'!$C$28>=BC23,'Dane wejściowe'!$C$28<BC24)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","98,6","0,78","2782,7/1401,3","18,20","1,92","3,03","2,59","1,12",false,0,0,null,null,1000,18,{"$f":"AND('Dane wejściowe'!$C$28>=BC24,'Dane wejściowe'!$C$28<BC25)","v":false},0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","95,7","0,78","2880,1/1471,4","18,20","1,92","3,03","2,96","1,21",false,0,0,null,null,null,null,null,{"$f":"SUM(BF6:BF24)","v":0}]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","93,1","0,78","2976,1/1541,4","18,20","1,92","3,03","3,22","1,31",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","90,6","0,78","3070,7/1611,5","18,20","1,92","3,03","3,50","1,40",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","88,2","0,78","3164,1/1681,5","18,20","1,92","3,03","3,78","1,51",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","85,9","0,78","3256,3/1751,6","18,20","1,92","3,03","4,07","1,61",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","83,8","0,78","3347,4/1821,7","18,20","1,92","3,03","4,37","1,72",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","81,7","0,78","3437,4/1891,7","18,20","1,92","3,03","4,69","1,83",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","79,7","0,78","3526,3/1961,8","18,20","1,92","3,03","5,01","1,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","77,9","0,78","3614,3/2031,9","18,20","1,92","3,03","5,34","2,06",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","76,1","0,78","3701,3/2101,9","18,20","1,92","3,03","5,68","2,18",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,31,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","74,4","0,78","3787,4/2172,0","18,20","1,92","3,03","6,03","2,30",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,32,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","72,7","0,78","3872,6/2242,1","18,20","1,92","3,03","6,39","2,42",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,33,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","71,1","0,78","3957,0/2312,1","18,20","1,92","3,03","6,76","2,55",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,34,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","69,6","0,78","4040,6/2382,2","18,20","1,92","3,03","7,14","2,68",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,35,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","68,1","0,78","4123,5/2452,3","18,20","1,92","3,03","7,53","2,81",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,36,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","66,7","0,78","4205,5/2522,3","18,20","1,92","3,03","7,92","2,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,37,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","65,4","0,78","4286,9/2592,4","18,20","1,92","3,03","8,33","3,08",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,38,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","64,0","0,78","4367,6/2662,5","18,20","1,92","3,03","8,74","3,22",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,39,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","62,8","0,78","4447,5/2732,5","18,20","1,92","3,03","9,17","3,36",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,40,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","61,5","0,78","4526,9/2802,6","18,20","1,92","3,03","9,60","3,50",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,41,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","60,3","0,78","4605,6/2872,6","18,20","1,92","3,03","10,05","3,65",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,42,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","59,2","0,78","4683,6/2942,7","18,20","1,92","3,03","10,50","3,79",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,43,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","58,0","0,78","4761,1/3012,8","18,20","1,92","3,03","10,96","3,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,44,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","56,9","0,78","4838,0/3082,8","18,20","1,92","3,03","11,43","4,10",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,45,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","55,9","0,78","4914,4/3152,9","18,20","1,92","3,03","11,91","4,25",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,46,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","54,8","0,78","4990,1/3223,0","18,20","1,92","3,03","12,40","4,41",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,47,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","53,8","0,78","5065,4/3293,0","18,20","1,92","3,03","12,89","4,57",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,48,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","52,8","0,78","5140,1/3363,1","18,20","1,92","3,03","13,40","4,73",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,49,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","51,9","0,78","5214,4/3433,2","18,20","1,92","3,03","13,91","4,89",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,50,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","50,9","0,78","5288,1/3503,2","18,20","1,92","3,03","14,43","5,06",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,51,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","50,0","0,78","5361,3/3573,3","18,20","1,92","3,03","14,97","5,23",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,52,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","49,2","0,78","5434,1/3643,4","18,20","1,92","3,03","15,51","5,40",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,53,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","48,3","0,78","5506,4/3713,4","18,20","1,92","3,03","16,05","5,83",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,54,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","47,4","0,78","5578,3/3783,5","18,20","1,92","3,03","16,61","6,04",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,55,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","46,6","0,78","5649,8/3853,6","18,20","1,92","3,03","17,18","6,24",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,56,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","45,8","0,78","5720,8/3923,6","18,20","1,92","3,03","17,75","6,45",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,57,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","45,0","0,78","5791,4/3993,7","18,20","1,92","3,03","18,34","6,66",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,58,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","44,2","0,78","5861,6/4063,7","18,20","1,92","3,03","18,93","6,88",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,59,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","43,5","0,78","5931,3/4133,8","18,20","1,92","3,03","19,53","7,10",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,60,null,"Woda",null,null,null,"Woda",null,null,null,70,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","42,7","0,78","6000,8/4203,9","18,20","1,92","3,03","20,14","7,32",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","307,7","0,78","317,7/77,9","16,37","2,44","3,37","0,02","0,01",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","234,5","0,78","521,3/155,8","16,37","2,44","3,37","0,05","0,03",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","198,0","0,78","696,6/233,7","16,37","2,44","3,37","0,09","0,05",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","174,6","0,78","855,9/311,7","16,37","2,44","3,37","0,15","0,08",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","157,7","0,78","1004,1/389,6","16,37","2,44","3,37","0,21","0,11",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","144,7","0,78","1144,0/467,5","16,37","2,44","3,37","0,29","0,15",{"$f":"AND(N70=$AY$4,X70=$AZ$4,Y70=$BA$4)","v":false},{"$f":"AX70*AV70","v":0},{"$f":"AX70*AW70","v":0}]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","134,2","0,78","1277,4/545,4","16,37","2,44","3,37","0,37","0,20",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","125,5","0,78","1405,5/623,3","16,37","2,44","3,37","0,47","0,25",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","118,1","0,78","1529,1/701,2","16,37","2,44","3,37","0,57","0,30",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","111,6","0,78","1648,8/779,2","16,37","2,44","3,37","0,67","0,36",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","105,9","0,78","1765,1/857,1","16,37","2,44","3,37","0,79","0,42",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","100,9","0,78","1878,3/935,0","16,37","2,44","3,37","0,91","0,48",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","96,4","0,78","1988,9/1012,9","16,37","2,44","3,37","1,04","0,55",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","92,2","0,78","2097,1/1090,8","16,37","2,44","3,37","1,17","0,62",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","88,5","0,78","2203,0/1168,7","16,37","2,44","3,37","1,31","0,69",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","85,0","0,78","2306,9/1246,7","16,37","2,44","3,37","1,46","0,77",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","81,9","0,78","2408,9/1324,6","16,37","2,44","3,37","1,61","0,85",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","78,9","0,78","2509,1/1402,5","16,37","2,44","3,37","1,77","0,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","76,2","0,78","2607,8/1480,4","16,37","2,44","3,37","1,94","1,03",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","73,6","0,78","2704,9/1558,3","16,37","2,44","3,37","2,11","1,12",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","71,2","0,78","2800,6/1636,2","16,37","2,44","3,37","2,29","1,21",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","68,9","0,78","2895,0/1714,1","16,37","2,44","3,37","2,47","1,31",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","66,7","0,78","2988,1/1792,1","16,37","2,44","3,37","2,65","1,40",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","64,7","0,78","3080,0/1870,0","16,37","2,44","3,37","2,98","1,51",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","62,8","0,78","3170,7/1947,9","16,37","2,44","3,37","3,21","1,61",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","60,9","0,78","3260,4/2025,8","16,37","2,44","3,37","3,45","1,72",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","59,2","0,78","3349,1/2103,7","16,37","2,44","3,37","3,69","1,83",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","57,5","0,78","3436,8/2181,6","16,37","2,44","3,37","3,95","1,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","55,9","0,78","3523,6/2259,6","16,37","2,44","3,37","4,21","2,06",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","54,4","0,78","3609,5/2337,5","16,37","2,44","3,37","4,48","2,18",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,31,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","53,0","0,78","3694,5/2415,4","16,37","2,44","3,37","4,75","2,30",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,32,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","51,6","0,78","3778,7/2493,3","16,37","2,44","3,37","5,04","2,42",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,33,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","50,2","0,78","3862,1/2571,2","16,37","2,44","3,37","5,33","2,55",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,34,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","48,9","0,78","3944,7/2649,1","16,37","2,44","3,37","5,63","2,68",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,35,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","47,7","0,78","4026,6/2727,1","16,37","2,44","3,37","5,93","2,81",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,36,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","46,4","0,78","4107,8/2805,0","16,37","2,44","3,37","6,24","2,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,37,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","45,3","0,78","4188,3/2882,9","16,37","2,44","3,37","6,56","3,08",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,38,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","44,2","0,78","4268,2/2960,8","16,37","2,44","3,37","6,89","3,22",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,39,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","43,1","0,78","4347,4/3038,7","16,37","2,44","3,37","7,23","3,36",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,40,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","42,0","0,78","4426,0/3116,6","16,37","2,44","3,37","7,57","3,50",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,41,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","41,0","0,78","4504,0/3194,6","16,37","2,44","3,37","7,92","3,65",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,42,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","40,0","0,78","4581,4/3272,5","16,37","2,44","3,37","8,27","3,79",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,43,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","39,0","0,78","4658,2/3350,4","16,37","2,44","3,37","8,64","3,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,44,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","38,1","0,78","4734,5/3428,3","16,37","2,44","3,37","9,01","4,10",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,45,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","37,2","0,78","4810,3/3506,2","16,37","2,44","3,37","9,39","4,25",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,46,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","36,3","0,78","4885,5/3584,1","16,37","2,44","3,37","9,77","4,41",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,47,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","35,5","0,78","4960,3/3662,0","16,37","2,44","3,37","10,16","4,57",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,48,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","34,6","0,78","5034,5/3740,0","16,37","2,44","3,37","10,56","4,73",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,49,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","33,8","0,78","5108,3/3817,9","16,37","2,44","3,37","10,96","4,89",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,50,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","33,0","0,78","5181,6/3895,8","16,37","2,44","3,37","11,38","5,06",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,51,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","32,2","0,78","5254,4/3973,7","16,37","2,44","3,37","11,80","5,23",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,52,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","31,5","0,78","5326,8/4051,6","16,37","2,44","3,37","12,22","5,40",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,53,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","30,7","0,78","5398,8/4129,5","16,37","2,44","3,37","12,65","5,83",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,54,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","30,0","0,78","5470,3/4207,5","16,37","2,44","3,37","13,09","6,04",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,55,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","29,3","0,78","5541,5/4285,4","16,37","2,44","3,37","13,54","6,24",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,56,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","28,6","0,78","5612,2/4363,3","16,37","2,44","3,37","13,99","6,45",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,57,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","28,0","0,78","5682,5/4441,2","16,37","2,44","3,37","14,45","6,66",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,58,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","27,3","0,78","5752,5/4519,1","16,37","2,44","3,37","14,92","6,88",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,59,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","26,6","0,78","5822,0/4597,0","16,37","2,44","3,37","15,39","7,10",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,60,null,"Woda",null,null,null,"Woda",null,null,null,70,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","26,0","0,78","5891,2/4675,0","16,37","2,44","3,37","15,87","7,32",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","245,3","0,78","305,3/88,4","14,43","3,12","3,83","0,01","0,01",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","184,1","0,78","502,4/176,8","14,43","3,12","3,83","0,04","0,03",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","153,6","0,78","672,8/265,2","14,43","3,12","3,83","0,08","0,05",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","134,1","0,78","827,8/353,6","14,43","3,12","3,83","0,12","0,08",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","120,0","0,78","972,4/442,1","14,43","3,12","3,83","0,18","0,11",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","109,1","0,78","1109,2/530,5","14,43","3,12","3,83","0,24","0,15",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","100,3","0,78","1239,7/618,9","14,43","3,12","3,83","0,31","0,20",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","93,0","0,78","1365,3/707,3","14,43","3,12","3,83","0,39","0,25",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","86,8","0,78","1486,5/795,7","14,43","3,12","3,83","0,47","0,30",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","81,4","0,78","1604,0/884,1","14,43","3,12","3,83","0,56","0,36",{"$f":"AND(N134=$AY$4,X134=$AZ$4,Y134=$BA$4)","v":false},{"$f":"AX134*AV134","v":0},{"$f":"AX134*AW134","v":0}]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","76,7","0,78","1718,4/972,5","14,43","3,12","3,83","0,66","0,42",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","72,5","0,78","1829,9/1060,9","14,43","3,12","3,83","0,76","0,48",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","68,7","0,78","1938,8/1149,4","14,43","3,12","3,83","0,87","0,55",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","65,2","0,78","2045,4/1237,8","14,43","3,12","3,83","0,98","0,62",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","62,1","0,78","2149,9/1326,2","14,43","3,12","3,83","1,10","0,69",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","59,2","0,78","2252,5/1414,6","14,43","3,12","3,83","1,22","0,77",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","56,6","0,78","2353,3/1503,0","14,43","3,12","3,83","1,35","0,85",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","54,1","0,78","2452,4/1591,4","14,43","3,12","3,83","1,48","0,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","51,8","0,78","2550,0/1679,8","14,43","3,12","3,83","1,62","1,03",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","49,7","0,78","2646,2/1768,2","14,43","3,12","3,83","1,76","1,12",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","47,6","0,78","2741,0/1856,6","14,43","3,12","3,83","1,91","1,21",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","45,7","0,78","2834,6/1945,1","14,43","3,12","3,83","2,06","1,31",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","43,9","0,78","2927,0/2033,5","14,43","3,12","3,83","2,22","1,40",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","42,2","0,78","3018,2/2121,9","14,43","3,12","3,83","2,38","1,51",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","40,6","0,78","3108,4/2210,3","14,43","3,12","3,83","2,54","1,61",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","39,1","0,78","3197,5/2298,7","14,43","3,12","3,83","2,71","1,72",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","37,6","0,78","3285,7/2387,1","14,43","3,12","3,83","2,89","1,83",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","36,3","0,78","3373,0/2475,5","14,43","3,12","3,83","3,07","1,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","34,9","0,78","3459,3/2563,9","14,43","3,12","3,83","3,41","2,06",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","33,6","0,78","3544,9/2652,3","14,43","3,12","3,83","3,63","2,18",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,31,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","32,4","0,78","3629,6/2740,8","14,43","3,12","3,83","3,86","2,30",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,32,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","31,3","0,78","3713,5/2829,2","14,43","3,12","3,83","4,09","2,42",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,33,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","30,1","0,78","3796,7/2917,6","14,43","3,12","3,83","4,32","2,55",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,34,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","29,0","0,78","3879,1/3006,0","14,43","3,12","3,83","4,56","2,68",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,35,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","28,0","0,78","3960,9/3094,4","14,43","3,12","3,83","4,81","2,81",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,36,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","27,0","0,78","4042,0/3182,8","14,43","3,12","3,83","5,07","2,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,37,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","26,0","0,78","4122,4/3271,2","14,43","3,12","3,83","5,33","3,08",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,38,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","25,1","0,78","4202,2/3359,6","14,43","3,12","3,83","5,59","3,22",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,39,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","24,2","0,78","4281,5/3448,1","14,43","3,12","3,83","5,86","3,36",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,40,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","23,3","0,78","4360,1/3536,5","14,43","3,12","3,83","6,14","3,50",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,41,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","22,4","0,78","4438,1/3624,9","14,43","3,12","3,83","6,43","3,65",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,42,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","21,6","0,78","4515,6/3713,3","14,43","3,12","3,83","6,71","3,79",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,43,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","20,8","0,78","4592,6/3801,7","14,43","3,12","3,83","7,01","3,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,44,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","20,0","0,78","4669,1/3890,1","14,43","3,12","3,83","7,31","4,10",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,45,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","19,3","0,78","4745,0/3978,5","14,43","3,12","3,83","7,62","4,25",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,46,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","18,5","0,78","4820,5/4066,9","14,43","3,12","3,83","7,93","4,41",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,47,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","17,8","0,78","4895,5/4155,3","14,43","3,12","3,83","8,25","4,57",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,48,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","17,1","0,78","4970,0/4243,8","14,43","3,12","3,83","8,57","4,73",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,49,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","16,4","0,78","5044,0/4332,2","14,43","3,12","3,83","8,90","4,89",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,50,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","15,8","0,78","5117,6/4420,6","14,43","3,12","3,83","9,23","5,06",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,51,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","15,1","0,78","5190,8/4509,0","14,43","3,12","3,83","9,57","5,23",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,52,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","14,5","0,78","5263,6/4597,4","14,43","3,12","3,83","9,92","5,40",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,53,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","13,9","0,78","5335,9/4685,8","14,43","3,12","3,83","10,27","5,83",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,54,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","13,3","0,78","5407,9/4774,2","14,43","3,12","3,83","10,62","6,04",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,55,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","12,7","0,78","5479,4/4862,6","14,43","3,12","3,83","10,99","6,24",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,56,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","12,1","0,78","5550,6/4951,1","14,43","3,12","3,83","11,35","6,45",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,57,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","11,5","0,78","5621,4/5039,5","14,43","3,12","3,83","11,73","6,66",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,58,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","11,0","0,78","5691,8/5127,9","14,43","3,12","3,83","12,11","6,88",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,59,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","10,5","0,78","5761,9/5216,3","14,43","3,12","3,83","12,49","7,10",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,60,null,"Woda",null,null,null,"Woda",null,null,null,70,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","9,9","0,78","5831,6/5304,7","14,43","3,12","3,83","12,88","7,32",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","184,8","0,78","294,5/103,4","12,33","4,06","4,48","0,01","0,01",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","135,2","0,78","486,5/206,9","12,33","4,06","4,48","0,03","0,03",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","110,5","0,78","653,2/310,3","12,33","4,06","4,48","0,07","0,05",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","94,6","0,78","805,3/413,7","12,33","4,06","4,48","0,11","0,08",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","83,2","0,78","947,5/517,2","12,33","4,06","4,48","0,15","0,11",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","74,4","0,78","1082,4/620,6","12,33","4,06","4,48","0,21","0,15",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","67,3","0,78","1211,4/724,0","12,33","4,06","4,48","0,27","0,20",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","61,4","0,78","1335,6/827,5","12,33","4,06","4,48","0,33","0,25",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","56,4","0,78","1455,7/930,9","12,33","4,06","4,48","0,40","0,30",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","52,0","0,78","1572,3/1034,3","12,33","4,06","4,48","0,48","0,36",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","48,2","0,78","1685,9/1137,8","12,33","4,06","4,48","0,56","0,42",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","44,8","0,78","1796,8/1241,2","12,33","4,06","4,48","0,65","0,48",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","41,7","0,78","1905,3/1344,7","12,33","4,06","4,48","0,74","0,55",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","38,9","0,78","2011,6/1448,1","12,33","4,06","4,48","0,83","0,62",{"$f":"AND(N198=$AY$4,X198=$AZ$4,Y198=$BA$4)","v":false},{"$f":"AX198*AV198","v":0},{"$f":"AX198*AW198","v":0}]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","36,4","0,78","2115,9/1551,5","12,33","4,06","4,48","0,93","0,69",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","34,0","0,78","2218,4/1655,0","12,33","4,06","4,48","1,04","0,77",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","31,9","0,78","2319,2/1758,4","12,33","4,06","4,48","1,15","0,85",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","29,9","0,78","2418,4/1861,8","12,33","4,06","4,48","1,26","0,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","28,0","0,78","2516,2/1965,3","12,33","4,06","4,48","1,38","1,03",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","26,3","0,78","2612,6/2068,7","12,33","4,06","4,48","1,50","1,12",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","24,7","0,78","2707,7/2172,1","12,33","4,06","4,48","1,63","1,21",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","23,1","0,78","2801,7/2275,6","12,33","4,06","4,48","1,76","1,31",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","21,7","0,78","2894,5/2379,0","12,33","4,06","4,48","1,89","1,40",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","20,3","0,78","2986,3/2482,4","12,33","4,06","4,48","2,03","1,51",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","19,0","0,78","3077,0/2585,9","12,33","4,06","4,48","2,17","1,61",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","17,8","0,78","3166,8/2689,3","12,33","4,06","4,48","2,31","1,72",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","16,6","0,78","3255,6/2792,7","12,33","4,06","4,48","2,46","1,83",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","15,4","0,78","3343,6/2896,2","12,33","4,06","4,48","2,61","1,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","14,4","0,78","3430,7/2999,6","12,33","4,06","4,48","2,77","2,06",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","13,3","0,78","3517,1/3103,0","12,33","4,06","4,48","2,93","2,18",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,31,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","12,4","0,78","3602,6/3206,5","12,33","4,06","4,48","3,09","2,30",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,32,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","11,4","0,78","3687,5/3309,9","12,33","4,06","4,48","3,26","2,42",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,33,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","10,5","0,78","3771,6/3413,4","12,33","4,06","4,48","3,59","2,55",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,34,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","9,6","0,78","3855,0/3516,8","12,33","4,06","4,48","3,79","2,68",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,35,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","8,8","0,78","3937,8/3620,2","12,33","4,06","4,48","4,00","2,81",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,36,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","8,0","0,78","4020,0/3723,7","12,33","4,06","4,48","4,21","2,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,37,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","7,2","0,78","4101,5/3827,1","12,33","4,06","4,48","4,42","3,08",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,38,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","6,4","0,78","4182,5/3930,5","12,33","4,06","4,48","4,64","3,22",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,39,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","5,7","0,78","4262,8/4034,0","12,33","4,06","4,48","4,87","3,36",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,40,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","5,0","0,78","4342,6/4137,4","12,33","4,06","4,48","5,10","3,50",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,41,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","4,3","0,78","4421,9/4240,8","12,33","4,06","4,48","5,33","3,65",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,42,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","3,6","0,78","4500,7/4344,3","12,33","4,06","4,48","5,57","3,79",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,43,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","3,0","0,78","4578,9/4447,7","12,33","4,06","4,48","5,82","3,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,44,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","2,3","0,78","4656,7/4551,1","12,33","4,06","4,48","6,07","4,10",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,45,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","1,7","0,78","4734,0/4654,6","12,33","4,06","4,48","6,32","4,25",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,46,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","1,1","0,78","4810,8/4758,0","12,33","4,06","4,48","6,58","4,41",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,47,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","0,5","0,78","4887,2/4861,4","12,33","4,06","4,48","6,85","4,57",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,48,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","0,0","0,78","4963,1/4964,9","12,33","4,06","4,48","7,11","4,73",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,49,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-0,6","0,78","5038,6/5068,3","12,33","4,06","4,48","7,39","4,89",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,50,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-1,1","0,78","5113,7/5171,7","12,33","4,06","4,48","7,66","5,06",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,51,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-1,6","0,78","5188,3/5275,2","12,33","4,06","4,48","7,95","5,23",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,52,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-2,2","0,78","5262,6/5378,6","12,33","4,06","4,48","8,23","5,40",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,53,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-2,7","0,78","5336,5/5482,1","12,33","4,06","4,48","8,52","5,83",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,54,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-3,1","0,78","5410,0/5585,5","12,33","4,06","4,48","8,82","6,04",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,55,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-3,6","0,78","5483,1/5688,9","12,33","4,06","4,48","9,12","6,24",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,56,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-4,1","0,78","5555,9/5792,4","12,33","4,06","4,48","9,43","6,45",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,57,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-4,5","0,78","5628,3/5895,8","12,33","4,06","4,48","9,74","6,66",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,58,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-5,0","0,78","5700,4/5999,2","12,33","4,06","4,48","10,05","6,88",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,59,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-5,4","0,78","5772,1/6102,7","12,33","4,06","4,48","10,37","7,10",false,0,0]
[0,1,0,0,1,1,1,"XB37","M",7,null,null,null,60,null,"Woda",null,null,null,"Woda",null,null,null,70,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-5,8","0,78","5843,5/6206,1","12,33","4,06","4,48","10,69","7,32",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","285,9","0,78","352,7/91,4","13,95","2,15","3,96","0,02","0,01",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","216,7","0,78","579,1/182,8","13,95","2,15","3,96","0,08","0,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","182,3","0,78","774,1/274,2","13,95","2,15","3,96","0,15","0,05",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","160,2","0,78","951,3/365,7","13,95","2,15","3,96","0,24","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","144,2","0,78","1116,3/457,1","13,95","2,15","3,96","0,35","0,11",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","131,9","0,78","1272,0/548,5","13,95","2,15","3,96","0,47","0,15",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","122,0","0,78","1420,6/639,9","13,95","2,15","3,96","0,60","0,20",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","113,7","0,78","1563,2/731,3","13,95","2,15","3,96","0,75","0,25",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","106,7","0,78","1700,8/822,7","13,95","2,15","3,96","0,91","0,30",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","100,6","0,78","1834,1/914,2","13,95","2,15","3,96","1,08","0,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","95,3","0,78","1963,6/1005,6","13,95","2,15","3,96","1,27","0,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","90,5","0,78","2089,8/1097,0","13,95","2,15","3,96","1,46","0,48",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","86,2","0,78","2212,9/1188,4","13,95","2,15","3,96","1,67","0,55",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","82,3","0,78","2333,4/1279,8","13,95","2,15","3,96","1,88","0,62",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","78,8","0,78","2451,3/1371,2","13,95","2,15","3,96","2,11","0,69",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","75,5","0,78","2567,1/1462,7","13,95","2,15","3,96","2,35","0,77",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","72,5","0,78","2680,7/1554,1","13,95","2,15","3,96","2,59","0,85",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","69,7","0,78","2792,4/1645,5","13,95","2,15","3,96","2,98","0,94",{"$f":"AND(N262=$AY$4,X262=$AZ$4,Y262=$BA$4)","v":false},{"$f":"AX262*AV262","v":0},{"$f":"AX262*AW262","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","67,1","0,78","2902,3/1736,9","13,95","2,15","3,96","3,29","1,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","64,7","0,78","3010,5/1828,3","13,95","2,15","3,96","3,61","1,12",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","62,4","0,78","3117,1/1919,7","13,95","2,15","3,96","3,95","1,21",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","60,2","0,78","3222,2/2011,2","13,95","2,15","3,96","4,30","1,31",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","58,2","0,78","3325,9/2102,6","13,95","2,15","3,96","4,66","1,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","56,3","0,78","3428,3/2194,0","13,95","2,15","3,96","5,04","1,51",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","54,4","0,78","3529,5/2285,4","13,95","2,15","3,96","5,43","1,61",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","52,7","0,78","3629,4/2376,8","13,95","2,15","3,96","5,83","1,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","51,0","0,78","3728,2/2468,2","13,95","2,15","3,96","6,25","1,83",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","49,5","0,78","3825,9/2559,7","13,95","2,15","3,96","6,68","1,94",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","48,0","0,78","3922,6/2651,1","13,95","2,15","3,96","7,12","2,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","46,5","0,78","4018,3/2742,5","13,95","2,15","3,96","7,58","2,18",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,31,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","45,1","0,78","4113,0/2833,9","13,95","2,15","3,96","8,04","2,30",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,32,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","43,8","0,78","4206,8/2925,3","13,95","2,15","3,96","8,52","2,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,33,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","42,5","0,78","4299,7/3016,7","13,95","2,15","3,96","9,02","2,55",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,34,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","41,3","0,78","4391,8/3108,2","13,95","2,15","3,96","9,52","2,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,35,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","40,1","0,78","4483,0/3199,6","13,95","2,15","3,96","10,04","2,81",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,36,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","39,0","0,78","4573,5/3291,0","13,95","2,15","3,96","10,57","2,94",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,37,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","37,9","0,78","4663,2/3382,4","13,95","2,15","3,96","11,11","3,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,38,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","36,8","0,78","4752,2/3473,8","13,95","2,15","3,96","11,66","3,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,39,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","35,8","0,78","4840,4/3565,2","13,95","2,15","3,96","12,23","3,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,40,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","34,8","0,78","4928,0/3656,7","13,95","2,15","3,96","12,81","3,50",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,41,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","33,8","0,78","5014,9/3748,1","13,95","2,15","3,96","13,40","3,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,42,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","32,9","0,78","5101,1/3839,5","13,95","2,15","3,96","14,00","3,79",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,43,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","31,9","0,78","5186,7/3930,9","13,95","2,15","3,96","14,62","3,94",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,44,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","31,1","0,78","5271,7/4022,3","13,95","2,15","3,96","15,25","4,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,45,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","30,2","0,78","5356,2/4113,7","13,95","2,15","3,96","15,88","4,25",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,46,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","29,4","0,78","5440,0/4205,1","13,95","2,15","3,96","16,54","4,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,47,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","28,6","0,78","5523,3/4296,6","13,95","2,15","3,96","17,20","4,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,48,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","27,8","0,78","5606,0/4388,0","13,95","2,15","3,96","17,87","4,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,49,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","27,0","0,78","5688,2/4479,4","13,95","2,15","3,96","18,56","4,89",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,50,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","26,2","0,78","5769,9/4570,8","13,95","2,15","3,96","19,26","5,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,51,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","25,5","0,78","5851,0/4662,2","13,95","2,15","3,96","19,96","5,23",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,52,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","24,8","0,78","5931,7/4753,6","13,95","2,15","3,96","20,68","5,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,53,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","24,1","0,78","6011,9/4845,1","13,95","2,15","3,96","21,42","5,83",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,54,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","23,4","0,78","6091,6/4936,5","13,95","2,15","3,96","22,16","6,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,55,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","22,7","0,78","6170,8/5027,9","13,95","2,15","3,96","22,92","6,24",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,56,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","22,1","0,78","6249,6/5119,3","13,95","2,15","3,96","23,68","6,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,57,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","21,4","0,78","6328,0/5210,7","13,95","2,15","3,96","24,46","6,66",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,58,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","20,8","0,78","6405,9/5302,1","13,95","2,15","3,96","25,25","6,88",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,59,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","20,2","0,78","6483,4/5393,6","13,95","2,15","3,96","26,05","7,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,60,null,"Woda",null,null,null,"Woda",null,null,null,65,35,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","19,6","0,78","6560,5/5485,0","13,95","2,15","3,96","26,86","7,32",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","229,6","0,78","338,4/102,6","12,43","2,82","4,44","0,02","0,01",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","171,4","0,78","557,1/205,3","12,43","2,82","4,44","0,06","0,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","142,3","0,78","746,2/307,9","12,43","2,82","4,44","0,12","0,05",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","123,7","0,78","918,4/410,6","12,43","2,82","4,44","0,19","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","110,3","0,78","1079,1/513,2","12,43","2,82","4,44","0,27","0,11",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","99,9","0,78","1231,1/615,9","12,43","2,82","4,44","0,37","0,15",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","91,5","0,78","1376,2/718,5","12,43","2,82","4,44","0,47","0,20",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","84,6","0,78","1515,7/821,1","12,43","2,82","4,44","0,59","0,25",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","78,7","0,78","1650,5/923,8","12,43","2,82","4,44","0,72","0,30",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","73,5","0,78","1781,2/1026,4","12,43","2,82","4,44","0,85","0,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","69,0","0,78","1908,3/1129,1","12,43","2,82","4,44","1,00","0,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","65,0","0,78","2032,3/1231,7","12,43","2,82","4,44","1,15","0,48",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","61,4","0,78","2153,4/1334,4","12,43","2,82","4,44","1,31","0,55",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","58,1","0,78","2272,0/1437,0","12,43","2,82","4,44","1,48","0,62",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","55,1","0,78","2388,2/1539,6","12,43","2,82","4,44","1,66","0,69",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","52,4","0,78","2502,3/1642,3","12,43","2,82","4,44","1,85","0,77",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","49,8","0,78","2614,4/1744,9","12,43","2,82","4,44","2,04","0,85",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","47,5","0,78","2724,7/1847,6","12,43","2,82","4,44","2,24","0,94",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","45,3","0,78","2833,3/1950,2","12,43","2,82","4,44","2,45","1,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","43,2","0,78","2940,2/2052,9","12,43","2,82","4,44","2,67","1,12",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","41,3","0,78","3045,7/2155,5","12,43","2,82","4,44","2,89","1,21",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","39,5","0,78","3149,8/2258,1","12,43","2,82","4,44","3,26","1,31",{"$f":"AND(N326=$AY$4,X326=$AZ$4,Y326=$BA$4)","v":false},{"$f":"AX326*AV326","v":0},{"$f":"AX326*AW326","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","37,8","0,78","3252,6/2360,8","12,43","2,82","4,44","3,54","1,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","36,2","0,78","3354,1/2463,4","12,43","2,82","4,44","3,83","1,51",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","34,6","0,78","3454,4/2566,1","12,43","2,82","4,44","4,12","1,61",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","33,2","0,78","3553,5/2668,7","12,43","2,82","4,44","4,43","1,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","31,8","0,78","3651,6/2771,4","12,43","2,82","4,44","4,75","1,83",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","30,4","0,78","3748,7/2874,0","12,43","2,82","4,44","5,07","1,94",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","29,2","0,78","3844,8/2976,6","12,43","2,82","4,44","5,41","2,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","28,0","0,78","3939,9/3079,3","12,43","2,82","4,44","5,75","2,18",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,31,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","26,8","0,78","4034,2/3181,9","12,43","2,82","4,44","6,11","2,30",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,32,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","25,7","0,78","4127,6/3284,6","12,43","2,82","4,44","6,47","2,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,33,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","24,6","0,78","4220,1/3387,2","12,43","2,82","4,44","6,85","2,55",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,34,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","23,6","0,78","4311,9/3489,9","12,43","2,82","4,44","7,23","2,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,35,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","22,6","0,78","4402,8/3592,5","12,43","2,82","4,44","7,62","2,81",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,36,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","21,6","0,78","4493,0/3695,1","12,43","2,82","4,44","8,02","2,94",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,37,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","20,7","0,78","4582,6/3797,8","12,43","2,82","4,44","8,44","3,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,38,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","19,8","0,78","4671,4/3900,4","12,43","2,82","4,44","8,86","3,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,39,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","18,9","0,78","4759,5/4003,1","12,43","2,82","4,44","9,29","3,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,40,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","18,1","0,78","4847,0/4105,7","12,43","2,82","4,44","9,73","3,50",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,41,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","17,2","0,78","4933,8/4208,4","12,43","2,82","4,44","10,17","3,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,42,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","16,4","0,78","5020,1/4311,0","12,43","2,82","4,44","10,63","3,79",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,43,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","15,7","0,78","5105,7/4413,6","12,43","2,82","4,44","11,10","3,94",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,44,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","14,9","0,78","5190,8/4516,3","12,43","2,82","4,44","11,58","4,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,45,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","14,2","0,78","5275,3/4618,9","12,43","2,82","4,44","12,06","4,25",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,46,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","13,5","0,78","5359,2/4721,6","12,43","2,82","4,44","12,55","4,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,47,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","12,8","0,78","5442,7/4824,2","12,43","2,82","4,44","13,06","4,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,48,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","12,2","0,78","5525,6/4926,9","12,43","2,82","4,44","13,57","4,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,49,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","11,5","0,78","5608,0/5029,5","12,43","2,82","4,44","14,09","4,89",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,50,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","10,9","0,78","5689,9/5132,1","12,43","2,82","4,44","14,62","5,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,51,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","10,2","0,78","5771,3/5234,8","12,43","2,82","4,44","15,16","5,23",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,52,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","9,6","0,78","5852,3/5337,4","12,43","2,82","4,44","15,70","5,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,53,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","9,1","0,78","5932,8/5440,1","12,43","2,82","4,44","16,26","5,83",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,54,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","8,5","0,78","6012,9/5542,7","12,43","2,82","4,44","16,83","6,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,55,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","7,9","0,78","6092,5/5645,3","12,43","2,82","4,44","17,40","6,24",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,56,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","7,4","0,78","6171,7/5748,0","12,43","2,82","4,44","17,98","6,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,57,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","6,8","0,78","6250,4/5850,6","12,43","2,82","4,44","18,57","6,66",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,58,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","6,3","0,78","6328,8/5953,3","12,43","2,82","4,44","19,17","6,88",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,59,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","5,8","0,78","6406,8/6055,9","12,43","2,82","4,44","19,78","7,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,60,null,"Woda",null,null,null,"Woda",null,null,null,65,30,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","5,3","0,78","6484,4/6158,6","12,43","2,82","4,44","20,40","7,32",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","176,8","0,78","326,2/117,9","10,82","3,70","5,10","0,02","0,01",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","128,7","0,78","539,1/235,8","10,82","3,70","5,10","0,05","0,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","104,7","0,78","723,9/353,6","10,82","3,70","5,10","0,10","0,05",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","89,3","0,78","892,7/471,5","10,82","3,70","5,10","0,15","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","78,2","0,78","1050,5/589,4","10,82","3,70","5,10","0,22","0,11",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","69,7","0,78","1200,2/707,3","10,82","3,70","5,10","0,30","0,15",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","62,8","0,78","1343,3/825,2","10,82","3,70","5,10","0,38","0,20",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","57,1","0,78","1481,1/943,1","10,82","3,70","5,10","0,48","0,25",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","52,2","0,78","1614,5/1060,9","10,82","3,70","5,10","0,58","0,30",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","47,9","0,78","1743,9/1178,8","10,82","3,70","5,10","0,69","0,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","44,2","0,78","1870,0/1296,7","10,82","3,70","5,10","0,81","0,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","40,9","0,78","1993,1/1414,6","10,82","3,70","5,10","0,94","0,48",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","37,9","0,78","2113,5/1532,5","10,82","3,70","5,10","1,07","0,55",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","35,2","0,78","2231,5/1650,4","10,82","3,70","5,10","1,21","0,62",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","32,7","0,78","2347,3/1768,2","10,82","3,70","5,10","1,35","0,69",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","30,5","0,78","2461,0/1886,1","10,82","3,70","5,10","1,50","0,77",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","28,4","0,78","2572,9/2004,0","10,82","3,70","5,10","1,66","0,85",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","26,4","0,78","2683,0/2121,9","10,82","3,70","5,10","1,82","0,94",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","24,6","0,78","2791,5/2239,8","10,82","3,70","5,10","1,99","1,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","22,9","0,78","2898,5/2357,6","10,82","3,70","5,10","2,17","1,12",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","21,4","0,78","3004,1/2475,5","10,82","3,70","5,10","2,35","1,21",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","19,9","0,78","3108,4/2593,4","10,82","3,70","5,10","2,54","1,31",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","18,4","0,78","3211,4/2711,3","10,82","3,70","5,10","2,73","1,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","17,1","0,78","3313,3/2829,2","10,82","3,70","5,10","2,93","1,51",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","15,8","0,78","3414,0/2947,1","10,82","3,70","5,10","3,13","1,61",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","14,6","0,78","3513,6/3064,9","10,82","3,70","5,10","3,34","1,72",{"$f":"AND(N390=$AY$4,X390=$AZ$4,Y390=$BA$4)","v":false},{"$f":"AX390*AV390","v":0},{"$f":"AX390*AW390","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","13,5","0,78","3612,2/3182,8","10,82","3,70","5,10","3,74","1,83",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","12,4","0,78","3709,8/3300,7","10,82","3,70","5,10","4,00","1,94",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","11,3","0,78","3806,5/3418,6","10,82","3,70","5,10","4,26","2,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","10,3","0,78","3902,4/3536,5","10,82","3,70","5,10","4,54","2,18",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,31,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","9,4","0,78","3997,3/3654,3","10,82","3,70","5,10","4,82","2,30",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,32,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","8,5","0,78","4091,5/3772,2","10,82","3,70","5,10","5,10","2,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,33,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","7,6","0,78","4184,8/3890,1","10,82","3,70","5,10","5,40","2,55",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,34,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","6,7","0,78","4277,4/4008,0","10,82","3,70","5,10","5,70","2,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,35,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","5,9","0,78","4369,3/4125,9","10,82","3,70","5,10","6,01","2,81",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,36,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","5,1","0,78","4460,4/4243,8","10,82","3,70","5,10","6,33","2,94",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,37,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","4,3","0,78","4550,9/4361,6","10,82","3,70","5,10","6,65","3,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,38,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","3,6","0,78","4640,7/4479,5","10,82","3,70","5,10","6,98","3,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,39,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","2,9","0,78","4729,9/4597,4","10,82","3,70","5,10","7,32","3,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,40,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","2,2","0,78","4818,5/4715,3","10,82","3,70","5,10","7,67","3,50",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,41,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","1,5","0,78","4906,4/4833,2","10,82","3,70","5,10","8,02","3,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,42,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","0,9","0,78","4993,8/4951,1","10,82","3,70","5,10","8,39","3,79",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,43,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","0,2","0,78","5080,7/5068,9","10,82","3,70","5,10","8,75","3,94",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,44,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-0,4","0,78","5166,9/5186,8","10,82","3,70","5,10","9,13","4,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,45,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-1,0","0,78","5252,7/5304,7","10,82","3,70","5,10","9,51","4,25",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,46,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-1,6","0,78","5337,9/5422,6","10,82","3,70","5,10","9,90","4,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,47,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-2,1","0,78","5422,6/5540,5","10,82","3,70","5,10","10,30","4,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,48,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-2,7","0,78","5506,9/5658,3","10,82","3,70","5,10","10,70","4,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,49,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-3,2","0,78","5590,6/5776,2","10,82","3,70","5,10","11,11","4,89",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,50,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-3,7","0,78","5673,9/5894,1","10,82","3,70","5,10","11,53","5,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,51,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-4,2","0,78","5756,8/6012,0","10,82","3,70","5,10","11,95","5,23",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,52,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-4,7","0,78","5839,2/6129,9","10,82","3,70","5,10","12,39","5,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,53,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-5,2","0,78","5921,1/6247,8","10,82","3,70","5,10","12,82","5,83",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,54,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-5,7","0,78","6002,7/6365,6","10,82","3,70","5,10","13,27","6,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,55,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-6,2","0,78","6083,8/6483,5","10,82","3,70","5,10","13,72","6,24",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,56,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-6,6","0,78","6164,5/6601,4","10,82","3,70","5,10","14,18","6,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,57,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-7,1","0,78","6244,9/6719,3","10,82","3,70","5,10","14,65","6,66",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,58,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-7,5","0,78","6324,8/6837,2","10,82","3,70","5,10","15,12","6,88",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,59,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-7,9","0,78","6404,4/6955,0","10,82","3,70","5,10","15,60","7,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,60,null,"Woda",null,null,null,"Woda",null,null,null,65,25,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-8,3","0,78","6483,6/7072,9","10,82","3,70","5,10","16,08","7,32",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","125,9","0,78","316,6/140,1","9,10","4,95","6,06","0,01","0,01",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","87,6","0,78","525,7/280,3","9,10","4,95","6,06","0,04","0,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","68,5","0,78","708,3/420,4","9,10","4,95","6,06","0,08","0,05",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","56,2","0,78","875,7/560,5","9,10","4,95","6,06","0,13","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","47,4","0,78","1032,7/700,6","9,10","4,95","6,06","0,18","0,11",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","40,6","0,78","1182,0/840,8","9,10","4,95","6,06","0,25","0,15",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","35,1","0,78","1325,1/980,9","9,10","4,95","6,06","0,32","0,20",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","30,5","0,78","1463,2/1121,0","9,10","4,95","6,06","0,40","0,25",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","26,6","0,78","1597,0/1261,2","9,10","4,95","6,06","0,49","0,30",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","23,3","0,78","1727,2/1401,3","9,10","4,95","6,06","0,58","0,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","20,3","0,78","1854,1/1541,4","9,10","4,95","6,06","0,68","0,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","17,6","0,78","1978,3/1681,5","9,10","4,95","6,06","0,78","0,48",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","15,3","0,78","2099,9/1821,7","9,10","4,95","6,06","0,89","0,55",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","13,1","0,78","2219,2/1961,8","9,10","4,95","6,06","1,01","0,62",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","11,2","0,78","2336,4/2101,9","9,10","4,95","6,06","1,13","0,69",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","9,3","0,78","2451,6/2242,1","9,10","4,95","6,06","1,26","0,77",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","7,7","0,78","2565,2/2382,2","9,10","4,95","6,06","1,39","0,85",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","6,1","0,78","2677,0/2522,3","9,10","4,95","6,06","1,52","0,94",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","4,7","0,78","2787,4/2662,5","9,10","4,95","6,06","1,67","1,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","3,3","0,78","2896,3/2802,6","9,10","4,95","6,06","1,81","1,12",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","2,1","0,78","3003,9/2942,7","9,10","4,95","6,06","1,97","1,21",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","0,9","0,78","3110,2/3082,8","9,10","4,95","6,06","2,12","1,31",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-0,2","0,78","3215,4/3223,0","9,10","4,95","6,06","2,28","1,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-1,3","0,78","3319,4/3363,1","9,10","4,95","6,06","2,45","1,51",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-2,3","0,78","3422,3/3503,2","9,10","4,95","6,06","2,62","1,61",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-3,3","0,78","3524,3/3643,4","9,10","4,95","6,06","2,79","1,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-4,2","0,78","3625,2/3783,5","9,10","4,95","6,06","2,97","1,83",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-5,1","0,78","3725,3/3923,6","9,10","4,95","6,06","3,16","1,94",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-5,9","0,78","3824,5/4063,7","9,10","4,95","6,06","3,35","2,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-6,7","0,78","3922,8/4203,9","9,10","4,95","6,06","3,54","2,18",{"$f":"AND(N454=$AY$4,X454=$AZ$4,Y454=$BA$4)","v":false},{"$f":"AX454*AV454","v":0},{"$f":"AX454*AW454","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,31,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-7,5","0,78","4020,3/4344,0","9,10","4,95","6,06","3,91","2,30",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,32,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-8,2","0,78","4117,1/4484,1","9,10","4,95","6,06","4,14","2,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,33,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-8,9","0,78","4213,1/4624,3","9,10","4,95","6,06","4,38","2,55",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,34,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-9,6","0,78","4308,4/4764,4","9,10","4,95","6,06","4,63","2,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,35,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-10,2","0,78","4403,0/4904,5","9,10","4,95","6,06","4,88","2,81",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,36,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-10,9","0,78","4496,9/5044,6","9,10","4,95","6,06","5,14","2,94",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,37,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-11,5","0,78","4590,2/5184,8","9,10","4,95","6,06","5,40","3,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,38,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-12,1","0,78","4682,8/5324,9","9,10","4,95","6,06","5,67","3,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,39,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-12,6","0,78","4774,9/5465,0","9,10","4,95","6,06","5,95","3,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,40,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-13,2","0,78","4866,4/5605,2","9,10","4,95","6,06","6,23","3,50",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,41,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-13,7","0,78","4957,3/5745,3","9,10","4,95","6,06","6,51","3,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,42,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-14,2","0,78","5047,7/5885,4","9,10","4,95","6,06","6,81","3,79",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,43,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-14,7","0,78","5137,5/6025,6","9,10","4,95","6,06","7,11","3,94",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,44,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-15,2","0,78","5226,8/6165,7","9,10","4,95","6,06","7,41","4,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,45,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-15,7","0,78","5315,6/6305,8","9,10","4,95","6,06","7,72","4,25",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,46,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-16,2","0,78","5403,9/6445,9","9,10","4,95","6,06","8,04","4,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,47,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-16,6","0,78","5491,8/6586,1","9,10","4,95","6,06","8,36","4,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,48,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-17,1","0,78","5579,2/6726,2","9,10","4,95","6,06","8,69","4,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,49,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-17,5","0,78","5666,1/6866,3","9,10","4,95","6,06","9,02","4,89",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,50,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-17,9","0,78","5752,6/7006,5","9,10","4,95","6,06","9,36","5,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,51,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-18,3","0,78","5838,7/7146,6","9,10","4,95","6,06","9,70","5,23",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,52,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-18,7","0,78","5924,3/7286,7","9,10","4,95","6,06","10,05","5,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,53,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-19,1","0,78","6009,5/7426,8","9,10","4,95","6,06","10,41","5,83",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,54,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-19,5","0,78","6094,4/7567,0","9,10","4,95","6,06","10,77","6,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,55,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-19,8","0,78","6178,8/7707,1","9,10","4,95","6,06","11,14","6,24",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,56,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-20,2","0,78","6262,9/7847,2","9,10","4,95","6,06","11,51","6,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,57,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-20,5","0,78","6346,6/7987,4","9,10","4,95","6,06","11,89","6,66",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,58,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-20,9","0,78","6429,9/8127,5","9,10","4,95","6,06","12,27","6,88",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,59,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-21,2","0,78","6512,9/8267,6","9,10","4,95","6,06","12,66","7,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,60,null,"Woda",null,null,null,"Woda",null,null,null,65,20,null,null,null,5,60,null,null,null,null,null,null,0,"XB37M-1-16 G 1 (20mm)","1*7M/1*8M","A","PED Art 4.3","-21,6","0,78","6595,5/8407,7","9,10","4,95","6,06","13,06","7,32",false,0,0]

{"sheet":"Arkusz3","index":3,"n_rows":26,"n_cols":10,"rows_kept":26,"cut":false,"hidden":true,"merged":[]}
[]
[null,"izolacja budynku",null,"temp siec zima",null,"temp instal",null,"temp siec lato",null,"temp siec lato powrot"]
[null,"TAK",null,130,null,90,null,70,null,35]
[null,"NIE",null,125,null,85,null,65,null,30]
[null,null,null,120,null,80,null,null,null,25]
[null,null,null,115,null,75,null,null,null,20]
[null,null,null,110,null,70]
[null,null,null,105]
[null,null,null,100]
[]
[]
[]
[]
[]
[null,null,"co",{"$f":"'Dane wejściowe'!C18","v":0},{"$f":"'Dane wejściowe'!C26","v":0},null,{"$f":"ROUND(MAX(D15,E15),2)","v":0}]
[null,null,"cwu",{"$f":"'Dane wejściowe'!C19","v":0},{"$f":"'Dane wejściowe'!C29","v":0},null,{"$f":"ROUND(MAX(D16,E16),2)","v":0}]
[]
[]
[]
[null,null,null,{"$f":"IF('Dane wejściowe'!C25=\"tak\",'Dane wejściowe'!C23*'Dane wejściowe'!C24*40,'Dane wejściowe'!C23*'Dane wejściowe'!C24*60)/1000","v":0}]
[null,null,null,{"$f":"IF('Dane wejściowe'!C28>0,('Dane wejściowe'!C28*90/1000)/'Wymienniki CWU'!BF25/3600*994.98*4.178*('Dane wejściowe'!C15-'Dane wejściowe'!C16)*(9.32*'Dane wejściowe'!C28^-0.244),0)","v":0}]
[]
[null,null,null,null,null,null,{"$f":"SUM(G24:G26)","v":{"$error":"#N/A"}}]
[null,null,null,{"$f":"(B25-18)","v":{"$error":"#N/A"}},8,null,{"$f":"IF(AND($D$24>0,$D$24<=8),E24)","v":{"$error":"#N/A"}}]
[null,{"$f":"'Projekt węzła'!E570","v":{"$error":"#N/A"}},null,null,12,null,{"$f":"IF(AND($D$24>8,$D$24<=12),E25)","v":{"$error":"#N/A"}}]
[null,null,null,null,18,null,{"$f":"IF(AND($D$24>12,$D$24<=18),E26)","v":{"$error":"#N/A"}}]

{"sheet":"PN-C.O.","index":4,"n_rows":46,"n_cols":14,"rows_kept":46,"cut":false,"hidden":true,"merged":[[42,1,42,8],[45,0,45,8],[1,1,1,8],[3,1,3,8],[14,1,14,2],[21,1,21,5],[32,4,32,6],[32,7,32,8]]}
[]
[null,"Dobór zaworu bezpieczeństwa dla obiegu c.o."]
[]
[null,"Obliczenia przeprowadzono zgodnie z p. 2.2.2. normy PN-B-02414:1999"]
[null,null,null,null," "]
[null,"Dobrano zawór bezpieczeństwa:"]
[null,"Typ",null,null,null,null,null,{"$f":"VLOOKUP(L17,ZB!A19:C122,3,FALSE)","v":1915},null,1,null,null,{"$f":"IF(H7=\"niestandardowe p1\",\"dla zaworów Flamco dostępne tylko ciśnienia nastawy zaworu 2,5 i 3 bar\",\" \")","v":" "}]
[null,"Średnica nominalna                                                                       ",null,null,null,null,null,{"$f":"CONCATENATE(\"DN \",H17)","v":"DN 25"},"mm",null,null,null,{"$f":"IF(H7=\"niestandardowe p1\",\"dla zaworów ARMAK dostępne tylko ciśnienia nastawy zaworu 2,5-5 bar\",\" \")","v":" "}]
[null,"Ilość zaworów",null,null,null,null,null,{"$f":"IF(54*SQRT((D34/(H22*SQRT(H18*H21))))/H10<=1,1,(IF(54*SQRT((D34/2/(H22*SQRT(H18*H21))))/H10<=1,2,(IF(54*SQRT((D34/3/(H22*SQRT(H18*H21))))/H10<=1,3,\"n > 3\")))))","v":{"$error":"#N/A"}},"szt.",null,null,null,{"$f":"IF(H9=\"n > 3\",\"liczba zaworów wieksza niż 3, zwiększ średnicę zaworu\",\" \")","v":{"$error":"#N/A"}}]
[null,"Min. średnica wewnętrzna",null,null,null,null,"d0",{"$f":"VLOOKUP(L17,ZB!A19:E122,5,FALSE)","v":20},"mm"]
[null,"Ciśnienie początku otwarcia",null,null,null,null,"p0",{"$f":"H18","v":2.5},"bar"]
[null,"Wsp. wypływu dla cieczy",null,null,null,null,"acrz",{"$f":"VLOOKUP(L17,ZB!A19:G122,7,FALSE)","v":0.41}]
[null,"Producent",null,null,null,null,null,{"$f":"H16","v":"HUSTY SYR"}]
[]
[null,"Założenia:",null,null,null,null,null,null,null,null,null,null,null,"UWAGA !"]
[null,"Producent ",null,null,null,null,null,{"$f":"INDEX(ZB!E2:E4,K16)","v":"HUSTY SYR"},null,null,1,null,null,"Dla zaworów SYR i FLAMCO dostepne średnice 25, 32, 40, 50 mm"]
[null,"Wstępnie zakładana średnica zaworu bezpieczeństwa",null,null,null,null,null,{"$f":"INDEX(ZB!D79:D87,K17)","v":25},"mm",null,1,{"$f":"CONCATENATE(H16,\" dn\",H17,\" \",H18,\"bar\")","v":"HUSTY SYR dn25 2,5bar"},null,"Dla zaworów ARMAK dostępne średnica 20x32, 25x40, 32x50, 40x65, 50x80 mm"]
[null,"Ciśnienie nastawy zaworu bezpieczeństwa",null,null,null,null,"p1",{"$f":"'Projekt węzła'!I294","v":2.5},"bar",null,6]
[null,"Ciśnienie nominalne sieci ciepłowniczej",null,null,null,null,"p2",16,"bar"]
[null,"Obliczeniowa temperatura wody sieciowej",null,null,null,null,null,{"$f":"'Projekt węzła'!I270","v":0},"0C",null,16]
[null,"Gęstość wody sieciowej przy jej obliczeniowej temp.",null,null,null,null,"r",{"$f":"VLOOKUP(H20,HEX!A230:B247,2,FALSE)","v":{"$error":"#N/A"}},"kg/m3"]
[null,"Dopuszczalny wsp. wypływu zaworu dla cieczy",null,null,null,null,"ac=0,9*acrz",{"$f":"PRODUCT(0.9*H12)","v":0.36899999999999999}]
[]
[]
[null,"Wymagana masowa przepustowość zaworu bezpieczeństwa [kg/s]",null,null,null,null,null,null," "]
[]
[]
[null,null,"b = 1","gdy    p2 - p1 ≤ 5 bar"]
[null,null,"b = 2","gdy    p2 - p1 > 5 bar"]
[]
[null,null,"p2 - p1 =",{"$f":"CONCATENATE(L31,\" bar\")","v":"13,5 bar"},"b =",{"$f":"IF(L31>5,2,1)","v":2},null,null,null,null,null,{"$f":"H19-H18","v":13.5}]
[]
[null,null,"A =",{"$f":"VLOOKUP(H33,HEX!A3:C109,3,FALSE)","v":1.5999999999999999E-5},"wg. karty katalogowej",null,null,"XB37L",null,null,26]
[null,null,"M = ",{"$f":"447.3*F31*D33*SQRT((L31*H21))","v":{"$error":"#N/A"}},"kg/s"]
[null,"Minimalna średnica wewnętrzna pojedynczego zaworu bezpieczeństwa:"]
[]
[]
[null,null,null,null,null,{"$f":"54*SQRT((D34/H9/(H22*SQRT(H18*H21))))","v":{"$error":"#N/A"}},"mm <  do   =",{"$f":"H10","v":20},"mm"]
[]
[]
[null,"Warunek: do > domin jest spełniony."]
[]
[null,"Dobrany zawór bezpieczeństwa spełnia wymagania normy PN-B-02414"]
[]
[]
["Danfoss Poland Sp. z o.o.\nTuchom ul. Tęczowa 46\n80-209 Chwaszczyno\ntel. 58/ 512 91 00\nfax. 58/ 512 91 05"]

{"sheet":"PN-NWP","index":5,"n_rows":55,"n_cols":14,"rows_kept":55,"cut":false,"hidden":true,"merged":[[1,0,1,8],[3,0,3,8],[54,0,54,8]]}
[]
["Dobór przeponowego naczynia wzbiorczego"]
[]
["Obliczenia przeprowadzono zgodnie z normą PN-B-02414:1999"]
[]
[null,"Dobrano naczynie wzbiorcze:"]
[null,"Typ",null,null,null,null,null,{"$f":"VLOOKUP(K7,NWP!A27:D110,3,FALSE)","v":{"$error":"#N/A"}},null,1,{"$f":"CONCATENATE(H18,H9)","v":{"$error":"#N/A"}}]
[null,"Ilość naczyń",null,null,null,null,null,{"$f":"N8","v":1},"szt.",null,null,null,null,1]
[null,"Pojemność naczynia                                     ",null,null,null,null,null,{"$f":"IF(H18=\"REFLEX\",NWP!O28,IF(H18=\"FLAMCO typ C\",NWP!O44,IF(H18=\"FLAMCO typ K\",NWP!O58,IF(H18=\"CIMM\",NWP!O66,IF(H18=\"VAREM\",NWP!O87,NWP!O95)))))","v":{"$error":"#N/A"}},"l"]
[null,"Wysokość",null,null,null,null,null,{"$f":"VLOOKUP(K7,NWP!A28:E110,5,FALSE)","v":{"$error":"#N/A"}},"mm"]
[null,"Średnica",null,null,null,null,null,{"$f":"VLOOKUP(K7,NWP!A28:F110,6,FALSE)","v":{"$error":"#N/A"}},"mm"]
[null,"Średnica przyłącza",null,null,null,null,null,{"$f":"VLOOKUP(K7,NWP!A28:H110,8,FALSE)","v":{"$error":"#N/A"}},"mm"]
[null,"Ciśnienie wstepne",null,null,null,null,null,{"$f":"E35","v":0.2},"bar"]
[null,"Producent",null,null,null,null,null,{"$f":"VLOOKUP(K7,NWP!A28:B110,2,FALSE)","v":{"$error":"#N/A"}}]
[]
[]
[null,"Założenia:"]
[null,"Producent ",null,null,null,null,null,"FERRO",null,null,null,null,1]
[null,"Pojemność instalacji",null,null,null,null,"V",{"$f":"'Projekt węzła'!I300","v":0},"m3"]
[null,"Maksymalne obliczeniowe ciśnienie w naczyniu",null,null,null,null,"pmax",{"$f":"'Projekt węzła'!I294","v":2.5},"bar"]
[null,"Ciśnienie statyczne w naczyniu",null,null,null,null,"pst",{"$f":"'Projekt węzła'!I298","v":0},"bar"]
[null,"Obliczeniowa temperatura na zasilaniu instalacji",null,null,null,null,"tz",{"$f":"'Projekt węzła'!I280","v":0},"oC",null,null,null,5]
[null,"Przyrost objętości wody instalacyjnej",null,null,null,null,"Dn",{"$f":"VLOOKUP(H22,NWP!G6:J17,4,FALSE)","v":{"$error":"#N/A"}},"l/kg"]
[null,"Gęstość wody instalacyjnej przy temp. T1=10oC",null,null,null,null,"r1",999.7,"kg/m3"]
[null,"Ilość naczyń",null,null,null,null,"n",{"$f":"H8","v":1}]
[]
[null,"Pojemność użytkowa naczynia Vu:"]
[]
[null,null,null,"Vu = V x r1 x Dn / n"]
[]
[null,null,null,"Vu =",{"$f":"H19*H24*H23/H8","v":{"$error":"#N/A"}},"dm3"]
[]
[null,"Ciśnienie wstępne w przestrzeni gazowej"]
[]
[null,null,null,"p=",{"$f":"H21+0.2","v":0.2},"bar"]
[]
[null,"Minimalna pojemność całkowita naczynia"]
[]
[]
[]
[]
[]
[null,null,null,"Vn=",{"$f":"E31*(H20+1)/(H20-E35)","v":{"$error":"#N/A"}},"dm3"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Danfoss Poland Sp. z o.o.\nTuchom ul. Tęczowa 46\n80-209 Chwaszczyno\ntel. 58/ 512 91 00\nfax. 58/ 512 91 05"]

{"sheet":"PN-C.W.U.","index":6,"n_rows":46,"n_cols":15,"rows_kept":46,"cut":false,"hidden":true,"merged":[[44,1,44,8],[45,0,45,8],[46,0,46,8],[1,1,1,8],[3,1,3,8],[16,1,16,2],[25,1,25,5],[33,4,33,6],[33,7,33,8]]}
[]
[null,"Dobór zaworu bezpieczeństwa dla obiegu c.w.u"]
[]
[null,"Obliczenia przeprowadzono zgodnie z p.. 3.2.5.2. normy PN-76/B-02440"]
[]
[null,"Dobrano zawór bezpieczeństwa:"]
[null,"Typ",null,null,null,null,null,{"$f":"VLOOKUP(M18,ZB!A135:C190,3,FALSE)","v":2115},null,1]
[null,"Średnica nominalna                                                                      ",null,null,null,null,null,{"$f":"CONCATENATE(\"DN \",H19)","v":"DN 20"},"mm"]
[null,"Ilość zaworów",null,null,null,null,null,{"$f":"IF(SQRT(((4*D36)/(3.14*1.59*H13*SQRT((1.1*H20-H21)/0.98*H24))))/H10<=1,1,(IF(SQRT(((4*D36/2)/(3.14*1.59*H13*SQRT((1.1*H20-H21)/0.98*H24))))/H10<=1,2,(IF(SQRT(((4*D36/3)/(3.14*1.59*H13*SQRT((1.1*H20-H21)/0.98*H24))))/H10<=1,3,\"n > 3\")))))","v":1},"szt.",null,null,null,null,{"$f":"IF(H9=\"n > 3\",\"liczba zaworów wieksza niż 3, zwiększ średnicę zaworu\",\" \")","v":" "}]
[null,"Min. średnica wewnętrzna",null,null,null,null,"d0",{"$f":"VLOOKUP(M18,ZB!A135:E190,5,FALSE)","v":14},"mm"]
[null,"Ciśnienie początku otwarcia",null,null,null,null,"p0",{"$f":"H20","v":6},"bar"]
[null,"Wsp. wypływu dla gazu dla dobranych zaworów",null,null,null,null,"a",{"$f":"VLOOKUP(M18,ZB!A135:G190,7,FALSE)","v":0.55000000000000004}]
[null,"ac dla dobranego zaworu",null,null,null,null,"ac=0,35*a",{"$f":"0.35*H12","v":0.1925}]
[null,"Wsp. wypływu wody grzejnej ",null,null,null,null,"ac1",1]
[null,"Producent",null,null,null,null,null,{"$f":"H18","v":"HUSTY SYR"}]
[]
[null,"Założenia:",null,null,null,null,null,null,null,null,null,null,null,null,"UWAGA !"]
[null,"Producent ",null,null,null,null,null,{"$f":"INDEX(ZB!F2:F3,K18)","v":"HUSTY SYR"},null,null,1,null,{"$f":"CONCATENATE(H18,\" dn\",H19,\" \",H20,\"bar\")","v":"HUSTY SYR dn20 6bar"},null,"Dla zaworów SYR dostepne średnice 20, 25, 32, 40, 50 mm"]
[null,"Wstępnie zakładana średnica zaworu bezpieczeństwa",null,null,null,null,null,20,"mm",null,2,null,null,null,"Dla zaworów ARMAK dostępne średnica 20x32, 25x40, 32x50, mm"]
[null,"Ciśnienie dopuszczalne instalacji cwu",null,null,null,null,"p1",6,"bar",null,4]
[null,"Ciśnienie na wylocie zaworu bezpieczeństwa",null,null,null,null,"p2",0,"bar"]
[null,"Ciśnienie czynnika grzejnego",null,null,null,null,"p3",16,"bar"]
[null,"Najniższa temperatura wody grzejnej na zasilaniu",null,null,null,null,"T1",{"$f":"'Projekt węzła'!I273","v":0},"0C",null,4]
[null,"Ciężar objętościowy wody przy jej obliczeniowej temperaturze",null,null,null,null,"g1",{"$f":"INDEX(HEX!B228:B247,K23)","v":977.81},"kg/m3"]
[]
[null,"Wymagana przepustowość zaworu bezp."]
[]
[]
[null,null,"b = 1","gdy p3 - p1 ≤ 5 kG/cm2",null,null,null,null,null,null,null,null,null,null,"1 kG/cm2 = 0,98 bar"]
[null,null,"b = 2","gdy p3 - p1 > 5 kG/cm2"]
[]
[null,null,"p3 - p1 =",{"$f":"CONCATENATE(L32,\" bar\")","v":"10 bar"},"b =",{"$f":"IF(L32>4.9,2,1)","v":2},null,null,null,null,null,{"$f":"H22-H20","v":10}]
[]
[null,null,"F =",{"$f":"VLOOKUP(H34,HEX!A3:B109,2,FALSE)","v":11},"wg. karty katalogowej",null,null,"XB37M",null,null,13]
[]
[null,null,"G = ",{"$f":"1.59*H14*F32*D34*SQRT(L32/0.98*H24)","v":3494.0893344010988},"kg/h"]
[]
[null,"Min. średnica wewn. dla pojedynczego zaworu bezp :"]
[]
[null,null,null,null,null,{"$f":"SQRT(((4*D36/H9)/(3.14*1.59*H13*SQRT((1.1*H20-H21)/0.98*H24))))","v":13.386750255700287},"mm < do =",{"$f":"H10","v":14},"mm"]
[]
[]
[null,"Warunek: do > domin jest spełniony."]
[]
[null,"Dobrany zawór bezpieczeństwa spełnia wymagania normy PN-76/B-02440"]
["Danfoss Poland Sp. z o.o.\nTuchom ul. Tęczowa 46\n80-209 Chwaszczyno\ntel. 58/ 512 91 00\nfax. 58/ 512 91 05"]

{"sheet":"Wymienniki CO","index":7,"n_rows":1054,"n_cols":54,"rows_kept":1054,"cut":false,"hidden":true,"merged":[]}
["Data","2017-09-09T10:13:13"]
["aplikacja","X Danfoss-XB",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"spadek po wys","spadek po nis"]
["Tryb","Sprawdzenie",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SUM(AY5:AY1054)","v":0},{"$f":"SUM(AZ5:AZ1054)","v":0},"temp zas siec","temp zas co"]
["isROT","Standardowy","Dozw. komb. płyt M Mieszanie płyt","Współprądowy","Równoległy","J.m.","Ilość stopni","Wymiennik ciepła","Typ płyty","Ilość kanałów kanału nr 1 Strona1","Ilość kanałów kanału nr 1 Strona2","Ilość kanałów kanału nr 2 Strona1","Ilość kanałów kanału nr 2 Strona2","Moc\n[kW]","Zapas powierzchni\n[%]","Czynnik Strona 1","Gaz1","Stężenie1\n[%]","Abs. Pressure1\n[bar]","Czynnik Strona 2","Gaz2","Stężenie2\n[%]","Abs. Pressure2\n[bar]","Temperatura na wlocie1\n[°C]","Temperatura na wylocie1\n[°C]","Masowe Natężenie przepływu1\n[kg/h]","Objętościowe Natężenie przepływu1\n[L/min]","Maks. spadek ciśnienia1\n[kPa]","Temperatura na wlocie2\n[°C]","Temperatura na wylocie2\n[°C]","Masowe Natężenie przepływu2\n[kg/h]","Objętościowe Natężenie przepływu2\n[L/min]","Maks. spadek ciśnienia2\n[kPa]","Masowe Natężenie przepływu Szer.-Równ.\n[kg/h]","Objętościowe Natężenie przepływu Szer.-Równ.\n[L/min]","Maks. spadek ciśnienia Szer.-Równ.\n[kPa]","FrameExtension(%)","Wymiennik ciepła","Grupowanie","Termin dostawy","PED","Zapas powierzchni\n[%]","Całkowita pow.\n[m^2]","HTC(Dostępny / Wymagany)\n[W/m^2-K]","LMTD\n[K]","NTU-1","NTU-2","Całkowity spadek ciśnienia-1\n[kPa]","Całkowity spadek ciśnienia-2\n[kPa]",null,null,{"$f":"ROUNDUP(Arkusz3!G15,0)","v":0},{"$f":"'Dane wejściowe'!C5","v":0},{"$f":"'Dane wejściowe'!C7","v":0}]
[0,0,0,0,1,1,1,"XB37","L",4,5,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","356,5","0,45","605,3/132,6","16,83","3,28","1,19","0,00","0,02",{"$f":"AND(N5=$AZ$4,X5=$BA$4,AD5=$BB$4)","v":false},{"$f":"AX5*AV5","v":0},{"$f":"AX5*AW5","v":0}]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","271,0","0,45","983,9/265,2","16,83","3,28","1,19","0,02","0,07",{"$f":"AND(N6=$AZ$4,X6=$BA$4,AD6=$BB$4)","v":false},{"$f":"AX6*AV6","v":0},{"$f":"AX6*AW6","v":0}]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","228,5","0,45","1306,9/397,9","16,83","3,28","1,19","0,04","0,16",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","201,2","0,45","1598,0/530,5","16,83","3,28","1,19","0,06","0,27",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","181,6","0,45","1867,3/663,1","16,83","3,28","1,19","0,09","0,40",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","166,5","0,45","2120,3/795,7","16,83","3,28","1,19","0,13","0,56",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","154,3","0,45","2360,4/928,3","16,83","3,28","1,19","0,17","0,74",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","144,1","0,45","2589,9/1060,9","16,83","3,28","1,19","0,21","0,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","135,5","0,45","2810,5/1193,6","16,83","3,28","1,19","0,26","1,17",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","128,0","0,45","3023,3/1326,2","16,83","3,28","1,19","0,32","1,42",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","121,4","0,45","3229,4/1458,8","16,83","3,28","1,19","0,38","1,69",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","115,5","0,45","3429,5/1591,4","16,83","3,28","1,19","0,44","1,98",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","110,2","0,45","3624,3/1724,0","16,83","3,28","1,19","0,51","2,30",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","105,5","0,45","3815,5/1856,6","16,83","3,28","1,19","0,59","2,63",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","101,3","0,45","4003,9/1989,3","16,83","3,28","1,19","0,67","2,98",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","97,5","0,45","4189,9/2121,9","16,83","3,28","1,19","0,75","3,36",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","94,0","0,45","4373,3/2254,5","16,83","3,28","1,19","0,84","3,66",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","90,7","0,45","4552,6/2387,1","16,83","3,28","1,19","0,93","4,09",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","87,5","0,45","4723,7/2519,7","16,83","3,28","1,19","1,03","4,54",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","84,4","0,45","4891,7/2652,3","16,83","3,28","1,19","1,13","5,01",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","81,6","0,45","5058,3/2785,0","16,83","3,28","1,19","1,23","5,51",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","79,0","0,45","5222,4/2917,6","16,83","3,28","1,19","1,34","6,02",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","76,5","0,45","5384,2/3050,2","16,83","3,28","1,19","1,46","6,56",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","74,2","0,45","5543,9/3182,8","16,83","3,28","1,19","1,58","7,13",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","72,0","0,45","5701,7/3315,4","16,83","3,28","1,19","1,70","7,71",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","69,8","0,45","5854,9/3448,1","16,83","3,28","1,19","1,82","8,32",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","67,8","0,45","6008,9/3580,7","16,83","3,28","1,19","1,95","8,95",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","65,9","0,45","6161,7/3713,3","16,83","3,28","1,19","2,09","9,60",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","64,0","0,45","6309,0/3845,9","16,83","3,28","1,19","2,17","10,27",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,130,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","62,3","0,45","6459,0/3978,5","16,83","3,28","1,19","2,32","10,96",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","336,4","0,45","631,9/144,8","15,42","3,25","1,30","0,01","0,02",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","254,8","0,45","1027,4/289,6","15,42","3,25","1,30","0,02","0,07",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","214,3","0,45","1365,0/434,4","15,42","3,25","1,30","0,04","0,16",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","188,2","0,45","1669,3/579,1","15,42","3,25","1,30","0,07","0,27",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","169,5","0,45","1951,0/723,9","15,42","3,25","1,30","0,11","0,40",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","155,0","0,45","2215,6/868,7","15,42","3,25","1,30","0,15","0,56",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","143,4","0,45","2466,7/1013,5","15,42","3,25","1,30","0,20","0,74",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","133,7","0,45","2706,8/1158,3","15,42","3,25","1,30","0,25","0,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","125,4","0,45","2937,6/1303,1","15,42","3,25","1,30","0,31","1,17",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","118,3","0,45","3160,3/1447,8","15,42","3,25","1,30","0,38","1,42",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","112,0","0,45","3376,0/1592,6","15,42","3,25","1,30","0,45","1,69",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","106,4","0,45","3585,4/1737,4","15,42","3,25","1,30","0,53","1,98",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","101,3","0,45","3789,2/1882,2","15,42","3,25","1,30","0,61","2,30",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","96,8","0,45","3989,7/2027,0","15,42","3,25","1,30","0,70","2,63",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","92,8","0,45","4187,5/2171,8","15,42","3,25","1,30","0,80","2,98",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","89,1","0,45","4381,2/2316,6","15,42","3,25","1,30","0,90","3,36",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","85,8","0,45","4573,6/2461,3","15,42","3,25","1,30","1,00","3,66",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","82,7","0,45","4761,5/2606,1","15,42","3,25","1,30","1,11","4,09",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","79,6","0,45","4940,6/2750,9","15,42","3,25","1,30","1,23","4,54",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","76,7","0,45","5118,1/2895,7","15,42","3,25","1,30","1,35","5,01",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","74,1","0,45","5292,9/3040,5","15,42","3,25","1,30","1,48","5,51",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","71,6","0,45","5465,2/3185,3","15,42","3,25","1,30","1,61","6,02",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","69,2","0,45","5635,2/3330,1","15,42","3,25","1,30","1,74","6,56",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","67,0","0,45","5803,2/3474,8","15,42","3,25","1,30","1,88","7,13",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","64,8","0,45","5965,8/3619,6","15,42","3,25","1,30","2,03","7,71",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","62,8","0,45","6129,8/3764,4","15,42","3,25","1,30","2,18","8,32",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","61,0","0,45","6292,6/3909,2","15,42","3,25","1,30","2,28","8,95",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","59,2","0,45","6454,7/4054,0","15,42","3,25","1,30","2,44","9,60",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","57,4","0,45","6609,0/4198,8","15,42","3,25","1,30","2,62","10,27",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,125,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","55,9","0,45","6769,5/4343,5","15,42","3,25","1,30","2,79","10,96",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","313,8","0,45","662,0/160,0","13,95","3,23","1,43","0,01","0,02",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","236,6","0,45","1077,0/320,0","13,95","3,23","1,43","0,02","0,07",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","198,2","0,45","1431,3/479,9","13,95","3,23","1,43","0,05","0,16",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","173,6","0,45","1750,9/639,9","13,95","3,23","1,43","0,09","0,27",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","155,9","0,45","2046,7/799,9","13,95","3,23","1,43","0,13","0,40",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","142,2","0,45","2324,7/959,9","13,95","3,23","1,43","0,18","0,56",{"$f":"AND(N70=$AZ$4,X70=$BA$4,AD70=$BB$4)","v":false},{"$f":"AX70*AV70","v":0},{"$f":"AX70*AW70","v":0}]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","131,2","0,45","2588,6/1119,8","13,95","3,23","1,43","0,24","0,74",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","122,0","0,45","2840,9/1279,8","13,95","3,23","1,43","0,31","0,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","114,2","0,45","3083,5/1439,8","13,95","3,23","1,43","0,38","1,17",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","107,4","0,45","3317,6/1599,8","13,95","3,23","1,43","0,46","1,42",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","101,4","0,45","3544,3/1759,8","13,95","3,23","1,43","0,55","1,69",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","96,1","0,45","3764,5/1919,7","13,95","3,23","1,43","0,65","1,98",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","91,3","0,45","3978,9/2079,7","13,95","3,23","1,43","0,75","2,30",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","87,0","0,45","4188,9/2239,7","13,95","3,23","1,43","0,86","2,63",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","83,2","0,45","4397,3/2399,7","13,95","3,23","1,43","0,97","2,98",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","79,8","0,45","4601,4/2559,7","13,95","3,23","1,43","1,09","3,36",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","76,7","0,45","4804,2/2719,6","13,95","3,23","1,43","1,22","3,66",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,7","0,45","5002,3/2879,6","13,95","3,23","1,43","1,36","4,09",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","70,8","0,45","5192,6/3039,6","13,95","3,23","1,43","1,50","4,54",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","68,1","0,45","5379,8/3199,6","13,95","3,23","1,43","1,64","5,01",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","65,6","0,45","5564,3/3359,5","13,95","3,23","1,43","1,80","5,51",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,3","0,45","5746,3/3519,5","13,95","3,23","1,43","1,96","6,02",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","61,1","0,45","5926,2/3679,5","13,95","3,23","1,43","2,12","6,56",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","59,0","0,45","6104,4/3839,5","13,95","3,23","1,43","2,29","7,13",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","56,9","0,45","6275,6/3999,5","13,95","3,23","1,43","2,41","7,71",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","55,1","0,45","6450,3/4159,4","13,95","3,23","1,43","2,60","8,32",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","53,4","0,45","6625,0/4319,4","13,95","3,23","1,43","2,80","8,95",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","51,6","0,45","6789,4/4479,4","13,95","3,23","1,43","3,00","9,60",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","50,1","0,45","6964,1/4639,4","13,95","3,23","1,43","3,21","10,27",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,120,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","48,4","0,45","7124,6/4799,4","13,95","3,23","1,43","3,43","10,96",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","288,0","0,45","696,9/179,6","12,43","3,22","1,61","0,01","0,02",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","215,8","0,45","1134,5/359,2","12,43","3,22","1,61","0,03","0,07",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","179,9","0,45","1508,4/538,9","12,43","3,22","1,61","0,06","0,16",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","156,9","0,45","1845,8/718,5","12,43","3,22","1,61","0,11","0,27",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","140,3","0,45","2158,3/898,1","12,43","3,22","1,61","0,16","0,40",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","127,5","0,45","2452,0/1077,7","12,43","3,22","1,61","0,23","0,56",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","117,2","0,45","2730,9/1257,4","12,43","3,22","1,61","0,30","0,74",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","108,6","0,45","2997,7/1437,0","12,43","3,22","1,61","0,38","0,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","101,3","0,45","3254,1/1616,6","12,43","3,22","1,61","0,48","1,17",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","94,9","0,45","3501,7/1796,2","12,43","3,22","1,61","0,58","1,42",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","89,4","0,45","3741,6/1975,9","12,43","3,22","1,61","0,69","1,69",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","84,4","0,45","3974,6/2155,5","12,43","3,22","1,61","0,81","1,98",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","79,9","0,45","4201,4/2335,1","12,43","3,22","1,61","0,93","2,30",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","75,9","0,45","4424,0/2514,7","12,43","3,22","1,61","1,07","2,63",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","72,4","0,45","4645,9/2694,4","12,43","3,22","1,61","1,21","2,98",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","69,2","0,45","4863,6/2874,0","12,43","3,22","1,61","1,36","3,36",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","66,4","0,45","5082,2/3053,6","12,43","3,22","1,61","1,52","3,66",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,5","0,45","5287,7/3233,2","12,43","3,22","1,61","1,69","4,09",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","60,9","0,45","5492,8/3412,9","12,43","3,22","1,61","1,87","4,54",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","58,5","0,45","5692,5/3592,5","12,43","3,22","1,61","2,05","5,01",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","56,0","0,45","5885,3/3772,1","12,43","3,22","1,61","2,24","5,51",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","53,8","0,45","6079,5/3951,7","12,43","3,22","1,61","2,44","6,02",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","51,8","0,45","6272,1/4131,4","12,43","3,22","1,61","2,58","6,56",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","49,9","0,45","6464,1/4311,0","12,43","3,22","1,61","2,80","7,13",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","48,0","0,45","6645,5/4490,6","12,43","3,22","1,61","3,03","7,71",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","46,4","0,45","6836,2/4670,2","12,43","3,22","1,61","3,27","8,32",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","44,6","0,45","7012,8/4849,9","12,43","3,22","1,61","3,52","8,95",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","42,9","0,45","7187,1/5029,5","12,43","3,22","1,61","3,78","9,60",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","41,3","0,45","7359,3/5209,1","12,43","3,22","1,61","4,04","10,27",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,115,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","39,7","0,45","7529,3/5388,7","12,43","3,22","1,61","4,31","10,96",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","257,7","0,45","737,9/206,3","10,82","3,24","1,85","0,01","0,02",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","191,5","0,45","1202,6/412,6","10,82","3,24","1,85","0,04","0,07",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","158,5","0,45","1600,0/618,9","10,82","3,24","1,85","0,08","0,16",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","137,4","0,45","1959,0/825,2","10,82","3,24","1,85","0,14","0,27",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","122,2","0,45","2291,5/1031,5","10,82","3,24","1,85","0,21","0,40",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","110,4","0,45","2604,3/1237,8","10,82","3,24","1,85","0,29","0,56",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","100,9","0,45","2901,5/1444,1","10,82","3,24","1,85","0,39","0,74",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","93,0","0,45","3185,8/1650,4","10,82","3,24","1,85","0,49","0,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","86,3","0,45","3459,2/1856,6","10,82","3,24","1,85","0,61","1,17",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","80,5","0,45","3723,3/2062,9","10,82","3,24","1,85","0,74","1,42",{"$f":"AND(N134=$AZ$4,X134=$BA$4,AD134=$BB$4)","v":false},{"$f":"AX134*AV134","v":0},{"$f":"AX134*AW134","v":0}]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","75,4","0,45","3979,2/2269,2","10,82","3,24","1,85","0,88","1,69",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","70,8","0,45","4227,8/2475,5","10,82","3,24","1,85","1,03","1,98",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","66,7","0,45","4469,9/2681,8","10,82","3,24","1,85","1,20","2,30",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,0","0,45","4708,0/2888,1","10,82","3,24","1,85","1,37","2,63",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","59,8","0,45","4943,7/3094,4","10,82","3,24","1,85","1,55","2,98",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","56,9","0,45","5179,6/3300,7","10,82","3,24","1,85","1,75","3,36",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","54,5","0,45","5417,0/3507,0","10,82","3,24","1,85","1,95","3,66",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","51,8","0,45","5638,0/3713,3","10,82","3,24","1,85","2,17","4,09",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","49,4","0,45","5855,9/3919,6","10,82","3,24","1,85","2,39","4,54",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","47,2","0,45","6071,3/4125,9","10,82","3,24","1,85","2,63","5,01",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","45,1","0,45","6285,2/4332,2","10,82","3,24","1,85","2,81","5,51",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","43,2","0,45","6499,2/4538,5","10,82","3,24","1,85","3,07","6,02",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","41,2","0,45","6699,0/4744,8","10,82","3,24","1,85","3,35","6,56",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","39,3","0,45","6895,9/4951,1","10,82","3,24","1,85","3,64","7,13",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","37,5","0,45","7090,0/5157,3","10,82","3,24","1,85","3,93","7,71",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","35,8","0,45","7281,4/5363,6","10,82","3,24","1,85","4,24","8,32",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","34,1","0,45","7470,4/5569,9","10,82","3,24","1,85","4,56","8,95",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","32,6","0,45","7656,9/5776,2","10,82","3,24","1,85","4,89","9,60",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","31,1","0,45","7841,1/5982,5","10,82","3,24","1,85","5,24","10,27",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,110,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","29,6","0,45","8023,2/6188,8","10,82","3,24","1,85","5,59","10,96",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","221,3","0,45","788,0/245,2","9,10","3,30","2,20","0,01","0,02",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","162,2","0,45","1286,1/490,5","9,10","3,30","2,20","0,05","0,07",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","132,8","0,45","1713,0/735,7","9,10","3,30","2,20","0,11","0,16",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","114,0","0,45","2099,0/980,9","9,10","3,30","2,20","0,19","0,27",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","100,4","0,45","2456,9/1226,1","9,10","3,30","2,20","0,28","0,40",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","89,9","0,45","2793,9/1471,4","9,10","3,30","2,20","0,39","0,56",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","81,4","0,45","3114,3/1716,6","9,10","3,30","2,20","0,51","0,74",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","74,4","0,45","3421,0/1961,8","9,10","3,30","2,20","0,66","0,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","68,4","0,45","3716,1/2207,0","9,10","3,30","2,20","0,81","1,17",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,2","0,45","4001,3/2452,3","9,10","3,30","2,20","0,99","1,42",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","58,6","0,45","4277,8/2697,5","9,10","3,30","2,20","1,17","1,69",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","54,5","0,45","4546,5/2942,7","9,10","3,30","2,20","1,38","1,98",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","50,8","0,45","4808,3/3187,9","9,10","3,30","2,20","1,59","2,30",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","47,6","0,45","5066,7/3433,2","9,10","3,30","2,20","1,82","2,63",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","44,9","0,45","5331,0/3678,4","9,10","3,30","2,20","2,07","2,98",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","42,4","0,45","5585,3/3923,6","9,10","3,30","2,20","2,33","3,36",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","40,2","0,45","5846,0/4168,8","9,10","3,30","2,20","2,60","3,66",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","37,9","0,45","6089,0/4414,1","9,10","3,30","2,20","2,81","4,09",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","35,9","0,45","6330,5/4659,3","9,10","3,30","2,20","3,12","4,54",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","33,7","0,45","6557,8/4904,5","9,10","3,30","2,20","3,45","5,01",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","31,7","0,45","6781,3/5149,7","9,10","3,30","2,20","3,79","5,51",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","29,8","0,45","7001,4/5395,0","9,10","3,30","2,20","4,15","6,02",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","28,0","0,45","7218,1/5640,2","9,10","3,30","2,20","4,52","6,56",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","26,3","0,45","7431,7/5885,4","9,10","3,30","2,20","4,90","7,13",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","24,7","0,45","7642,4/6130,6","9,10","3,30","2,20","5,31","7,71",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","23,1","0,45","7850,3/6375,9","9,10","3,30","2,20","5,72","8,32",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","21,7","0,45","8055,5/6621,1","9,10","3,30","2,20","6,16","8,95",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","20,3","0,45","8258,1/6866,3","9,10","3,30","2,20","6,60","9,60",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","18,9","0,45","8458,3/7111,6","9,10","3,30","2,20","7,07","10,27",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,105,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","17,7","0,45","8656,2/7356,8","9,10","3,30","2,20","7,54","10,96",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","175,4","0,45","852,3/309,4","7,21","3,47","2,77","0,02","0,02",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","125,4","0,45","1395,0/618,9","7,21","3,47","2,77","0,07","0,07",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","100,5","0,45","1861,5/928,3","7,21","3,47","2,77","0,15","0,16",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","84,5","0,45","2284,2/1237,8","7,21","3,47","2,77","0,26","0,27",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,0","0,45","2677,0/1547,2","7,21","3,47","2,77","0,39","0,40",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","64,1","0,45","3047,2/1856,6","7,21","3,47","2,77","0,54","0,56",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","57,0","0,45","3399,7/2166,1","7,21","3,47","2,77","0,72","0,74",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","51,0","0,45","3737,5/2475,5","7,21","3,47","2,77","0,92","0,94",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","45,9","0,45","4062,9/2785,0","7,21","3,47","2,77","1,14","1,17",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","41,5","0,45","4377,7/3094,4","7,21","3,47","2,77","1,38","1,42",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","37,6","0,45","4683,1/3403,8","7,21","3,47","2,77","1,65","1,69",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","34,1","0,45","4980,3/3713,3","7,21","3,47","2,77","1,93","1,98",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","31,1","0,45","5274,3/4022,7","7,21","3,47","2,77","2,23","2,30",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","28,6","0,45","5572,8/4332,2","7,21","3,47","2,77","2,56","2,63",{"$f":"AND(N198=$AZ$4,X198=$BA$4,AD198=$BB$4)","v":false},{"$f":"AX198*AV198","v":0},{"$f":"AX198*AW198","v":0}]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","26,3","0,45","5862,5/4641,6","7,21","3,47","2,77","2,90","2,98",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","24,4","0,45","6157,3/4951,1","7,21","3,47","2,77","3,19","3,36",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","22,3","0,45","6433,3/5260,5","7,21","3,47","2,77","3,59","3,66",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","20,2","0,45","6694,7/5569,9","7,21","3,47","2,77","4,01","4,09",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","18,2","0,45","6951,5/5879,4","7,21","3,47","2,77","4,45","4,54",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","16,4","0,45","7204,0/6188,8","7,21","3,47","2,77","4,91","5,01",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","14,7","0,45","7452,6/6498,3","7,21","3,47","2,77","5,40","5,51",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","13,1","0,45","7697,4/6807,7","7,21","3,47","2,77","5,90","6,02",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","11,5","0,45","7938,7/7117,1","7,21","3,47","2,77","6,43","6,56",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","10,1","0,45","8176,7/7426,6","7,21","3,47","2,77","6,98","7,13",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","8,7","0,45","8411,5/7736,0","7,21","3,47","2,77","7,56","7,71",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","7,4","0,45","8643,3/8045,5","7,21","3,47","2,77","8,15","8,32",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","6,2","0,45","8872,2/8354,9","7,21","3,47","2,77","8,77","8,95",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","5,0","0,45","9098,4/8664,3","7,21","3,47","2,77","9,40","9,60",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","3,9","0,45","9322,0/8973,8","7,21","3,47","2,77","10,06","10,27",false,0,0]
[0,1,0,0,1,1,1,"XB37","L",4,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,100,75,null,null,null,70,90,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","2,8","0,45","9543,1/9283,2","7,21","3,47","2,77","10,74","10,96",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","365,3","0,45","570,5/122,6","18,20","3,30","1,10","0,00","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","278,2","0,45","927,4/245,2","18,20","3,30","1,10","0,01","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","234,9","0,45","1231,8/367,8","18,20","3,30","1,10","0,03","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","207,1","0,45","1506,3/490,5","18,20","3,30","1,10","0,05","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","187,1","0,45","1760,3/613,1","18,20","3,30","1,10","0,08","0,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","171,7","0,45","1999,0/735,7","18,20","3,30","1,10","0,11","0,56",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","159,3","0,45","2225,5/858,3","18,20","3,30","1,10","0,14","0,75",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","149,0","0,45","2442,0/980,9","18,20","3,30","1,10","0,18","0,95",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","140,2","0,45","2650,1/1103,5","18,20","3,30","1,10","0,22","1,18",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","132,5","0,45","2851,0/1226,1","18,20","3,30","1,10","0,27","1,43",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","125,8","0,45","3045,5/1348,7","18,20","3,30","1,10","0,32","1,71",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","119,8","0,45","3234,4/1471,4","18,20","3,30","1,10","0,38","2,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","114,5","0,45","3418,3/1594,0","18,20","3,30","1,10","0,44","2,32",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","109,6","0,45","3597,6/1716,6","18,20","3,30","1,10","0,50","2,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","105,2","0,45","3773,9/1839,2","18,20","3,30","1,10","0,57","3,01",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","101,3","0,45","3948,5/1961,8","18,20","3,30","1,10","0,64","3,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","97,6","0,45","4118,9/2084,4","18,20","3,30","1,10","0,72","3,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","94,4","0,45","4290,5/2207,0","18,20","3,30","1,10","0,80","4,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","91,3","0,45","4456,8/2329,6","18,20","3,30","1,10","0,88","4,55",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","88,2","0,45","4615,6/2452,3","18,20","3,30","1,10","0,97","5,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","85,3","0,45","4771,7/2574,9","18,20","3,30","1,10","1,06","5,52",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","82,6","0,45","4925,3/2697,5","18,20","3,30","1,10","1,15","6,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","80,1","0,45","5077,7/2820,1","18,20","3,30","1,10","1,25","6,58",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","77,7","0,45","5228,1/2942,7","18,20","3,30","1,10","1,35","7,15",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","75,4","0,45","5376,5/3065,3","18,20","3,30","1,10","1,45","7,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,3","0,45","5523,2/3187,9","18,20","3,30","1,10","1,56","8,34",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","71,2","0,45","5666,1/3310,6","18,20","3,30","1,10","1,67","8,97",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","69,2","0,45","5809,3/3433,2","18,20","3,30","1,10","1,79","9,63",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","67,4","0,45","5951,0/3555,8","18,20","3,30","1,10","1,91","10,30",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,130,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","65,5","0,45","6088,7/3678,4","18,20","3,30","1,10","2,03","11,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","347,7","0,45","593,7/132,6","16,83","3,27","1,19","0,00","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","263,9","0,45","965,3/265,2","16,83","3,27","1,19","0,02","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","222,3","0,45","1282,5/397,9","16,83","3,27","1,19","0,04","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","195,7","0,45","1568,5/530,5","16,83","3,27","1,19","0,06","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","176,5","0,45","1833,1/663,1","16,83","3,27","1,19","0,09","0,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","161,6","0,45","2081,9/795,7","16,83","3,27","1,19","0,13","0,56",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","149,7","0,45","2317,9/928,3","16,83","3,27","1,19","0,17","0,75",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","139,8","0,45","2543,7/1060,9","16,83","3,27","1,19","0,21","0,95",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","131,3","0,45","2760,6/1193,6","16,83","3,27","1,19","0,26","1,18",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","124,0","0,45","2970,0/1326,2","16,83","3,27","1,19","0,32","1,43",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","117,5","0,45","3172,9/1458,8","16,83","3,27","1,19","0,38","1,71",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","111,8","0,45","3369,8/1591,4","16,83","3,27","1,19","0,45","2,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","106,6","0,45","3561,6/1724,0","16,83","3,27","1,19","0,52","2,32",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","101,9","0,45","3748,5/1856,6","16,83","3,27","1,19","0,59","2,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","97,7","0,45","3932,6/1989,3","16,83","3,27","1,19","0,67","3,01",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","93,9","0,45","4114,2/2121,9","16,83","3,27","1,19","0,76","3,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","90,5","0,45","4293,9/2254,5","16,83","3,27","1,19","0,85","3,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","87,3","0,45","4471,4/2387,1","16,83","3,27","1,19","0,94","4,10",{"$f":"AND(N262=$AZ$4,X262=$BA$4,AD262=$BB$4)","v":false},{"$f":"AX262*AV262","v":0},{"$f":"AX262*AW262","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","84,3","0,45","4645,1/2519,7","16,83","3,27","1,19","1,04","4,55",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","81,4","0,45","4810,7/2652,3","16,83","3,27","1,19","1,14","5,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","78,6","0,45","4973,5/2785,0","16,83","3,27","1,19","1,24","5,52",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","76,0","0,45","5135,1/2917,6","16,83","3,27","1,19","1,35","6,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,6","0,45","5294,5/3050,2","16,83","3,27","1,19","1,47","6,58",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","71,3","0,45","5451,7/3182,8","16,83","3,27","1,19","1,59","7,15",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","69,1","0,45","5607,0/3315,4","16,83","3,27","1,19","1,71","7,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","67,0","0,45","5758,1/3448,1","16,83","3,27","1,19","1,84","8,34",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","65,0","0,45","5909,6/3580,7","16,83","3,27","1,19","1,97","8,97",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,2","0,45","6059,8/3713,3","16,83","3,27","1,19","2,10","9,63",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","61,3","0,45","6205,1/3845,9","16,83","3,27","1,19","2,24","10,30",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,125,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","59,7","0,45","6352,3/3978,5","16,83","3,27","1,19","2,39","11,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","328,0","0,45","619,7/144,8","15,42","3,25","1,30","0,01","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","248,1","0,45","1008,0/289,6","15,42","3,25","1,30","0,02","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","208,4","0,45","1339,5/434,4","15,42","3,25","1,30","0,04","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","182,9","0,45","1638,6/579,1","15,42","3,25","1,30","0,07","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","164,6","0,45","1915,4/723,9","15,42","3,25","1,30","0,11","0,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","150,4","0,45","2175,5/868,7","15,42","3,25","1,30","0,15","0,56",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","139,0","0,45","2422,5/1013,5","15,42","3,25","1,30","0,20","0,75",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","129,5","0,45","2658,6/1158,3","15,42","3,25","1,30","0,26","0,95",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","121,5","0,45","2885,7/1303,1","15,42","3,25","1,30","0,32","1,18",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","114,4","0,45","3104,8/1447,8","15,42","3,25","1,30","0,38","1,43",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","108,3","0,45","3317,1/1592,6","15,42","3,25","1,30","0,46","1,71",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","102,8","0,45","3523,2/1737,4","15,42","3,25","1,30","0,54","2,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","97,8","0,45","3723,9/1882,2","15,42","3,25","1,30","0,62","2,32",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","93,4","0,45","3919,6/2027,0","15,42","3,25","1,30","0,71","2,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","89,4","0,45","4112,6/2171,8","15,42","3,25","1,30","0,81","3,01",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","85,8","0,45","4303,4/2316,6","15,42","3,25","1,30","0,91","3,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","82,4","0,45","4490,6/2461,3","15,42","3,25","1,30","1,01","3,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","79,5","0,45","4676,8/2606,1","15,42","3,25","1,30","1,12","4,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","76,6","0,45","4858,9/2750,9","15,42","3,25","1,30","1,24","4,55",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,8","0,45","5032,3/2895,7","15,42","3,25","1,30","1,36","5,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","71,2","0,45","5204,4/3040,5","15,42","3,25","1,30","1,49","5,52",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","68,7","0,45","5374,1/3185,3","15,42","3,25","1,30","1,62","6,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","66,4","0,45","5541,4/3330,1","15,42","3,25","1,30","1,76","6,58",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","64,2","0,45","5706,6/3474,8","15,42","3,25","1,30","1,90","7,15",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","62,2","0,45","5870,1/3619,6","15,42","3,25","1,30","2,05","7,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","60,1","0,45","6028,3/3764,4","15,42","3,25","1,30","2,20","8,34",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","58,3","0,45","6188,1/3909,2","15,42","3,25","1,30","2,36","8,97",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","56,6","0,45","6346,8/4054,0","15,42","3,25","1,30","2,52","9,63",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","54,8","0,45","6499,1/4198,8","15,42","3,25","1,30","2,62","10,30",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,120,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","53,2","0,45","6655,4/4343,5","15,42","3,25","1,30","2,80","11,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","305,9","0,45","649,3/160,0","13,95","3,23","1,43","0,01","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","230,3","0,45","1056,7/320,0","13,95","3,23","1,43","0,02","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","192,7","0,45","1404,7/479,9","13,95","3,23","1,43","0,05","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","168,6","0,45","1718,7/639,9","13,95","3,23","1,43","0,09","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","151,2","0,45","2009,5/799,9","13,95","3,23","1,43","0,13","0,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","137,8","0,45","2282,8/959,9","13,95","3,23","1,43","0,18","0,56",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","127,0","0,45","2542,4/1119,8","13,95","3,23","1,43","0,24","0,75",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","118,0","0,45","2790,6/1279,8","13,95","3,23","1,43","0,31","0,95",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","110,4","0,45","3029,2/1439,8","13,95","3,23","1,43","0,39","1,18",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","103,8","0,45","3259,6/1599,8","13,95","3,23","1,43","0,47","1,43",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","97,9","0,45","3482,9/1759,8","13,95","3,23","1,43","0,56","1,71",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","92,7","0,45","3699,7/1919,7","13,95","3,23","1,43","0,65","2,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","88,0","0,45","3910,7/2079,7","13,95","3,23","1,43","0,76","2,32",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","83,8","0,45","4116,6/2239,7","13,95","3,23","1,43","0,86","2,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","80,0","0,45","4320,1/2399,7","13,95","3,23","1,43","0,98","3,01",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","76,6","0,45","4519,9/2559,7","13,95","3,23","1,43","1,10","3,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,4","0,45","4717,2/2719,6","13,95","3,23","1,43","1,23","3,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","70,6","0,45","4913,6/2879,6","13,95","3,23","1,43","1,37","4,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","68,0","0,45","5105,6/3039,6","13,95","3,23","1,43","1,51","4,55",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","65,3","0,45","5289,9/3199,6","13,95","3,23","1,43","1,66","5,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","62,9","0,45","5471,5/3359,5","13,95","3,23","1,43","1,81","5,52",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","60,6","0,45","5650,7/3519,5","13,95","3,23","1,43","1,97","6,04",{"$f":"AND(N326=$AZ$4,X326=$BA$4,AD326=$BB$4)","v":false},{"$f":"AX326*AV326","v":0},{"$f":"AX326*AW326","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","58,4","0,45","5827,6/3679,5","13,95","3,23","1,43","2,14","6,58",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","56,3","0,45","6002,6/3839,5","13,95","3,23","1,43","2,31","7,15",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","54,3","0,45","6171,5/3999,5","13,95","3,23","1,43","2,49","7,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","52,5","0,45","6342,7/4159,4","13,95","3,23","1,43","2,68","8,34",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","50,8","0,45","6513,0/4319,4","13,95","3,23","1,43","2,81","8,97",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","49,0","0,45","6675,3/4479,4","13,95","3,23","1,43","3,01","9,63",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","47,5","0,45","6843,8/4639,4","13,95","3,23","1,43","3,22","10,30",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,115,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","45,9","0,45","7002,3/4799,4","13,95","3,23","1,43","3,44","11,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","280,5","0,45","683,5/179,6","12,43","3,22","1,61","0,01","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","209,8","0,45","1113,1/359,2","12,43","3,22","1,61","0,03","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","174,7","0,45","1480,4/538,9","12,43","3,22","1,61","0,06","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","152,2","0,45","1812,0/718,5","12,43","3,22","1,61","0,11","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","136,0","0,45","2119,2/898,1","12,43","3,22","1,61","0,16","0,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","123,4","0,45","2408,0/1077,7","12,43","3,22","1,61","0,23","0,56",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","113,3","0,45","2682,4/1257,4","12,43","3,22","1,61","0,30","0,75",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","104,9","0,45","2944,9/1437,0","12,43","3,22","1,61","0,39","0,95",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","97,8","0,45","3197,3/1616,6","12,43","3,22","1,61","0,48","1,18",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","91,6","0,45","3441,0/1796,2","12,43","3,22","1,61","0,58","1,43",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","86,1","0,45","3677,2/1975,9","12,43","3,22","1,61","0,69","1,71",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","81,2","0,45","3906,6/2155,5","12,43","3,22","1,61","0,81","2,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","76,9","0,45","4130,0/2335,1","12,43","3,22","1,61","0,94","2,32",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","72,9","0,45","4348,0/2514,7","12,43","3,22","1,61","1,08","2,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","69,4","0,45","4564,0/2694,4","12,43","3,22","1,61","1,22","3,01",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","66,2","0,45","4776,7/2874,0","12,43","3,22","1,61","1,37","3,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,3","0,45","4987,2/3053,6","12,43","3,22","1,61","1,54","3,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","60,6","0,45","5192,3/3233,2","12,43","3,22","1,61","1,70","4,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","58,2","0,45","5400,8/3412,9","12,43","3,22","1,61","1,88","4,55",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","55,8","0,45","5597,2/3592,5","12,43","3,22","1,61","2,07","5,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","53,4","0,45","5787,4/3772,1","12,43","3,22","1,61","2,26","5,52",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","51,3","0,45","5978,2/3951,7","12,43","3,22","1,61","2,46","6,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","49,3","0,45","6167,1/4131,4","12,43","3,22","1,61","2,67","6,58",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","47,4","0,45","6354,6/4311,0","12,43","3,22","1,61","2,81","7,15",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","45,5","0,45","6533,7/4490,6","12,43","3,22","1,61","3,04","7,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","43,9","0,45","6718,4/4670,2","12,43","3,22","1,61","3,28","8,34",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","42,4","0,45","6904,8/4849,9","12,43","3,22","1,61","3,53","8,97",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","40,7","0,45","7076,9/5029,5","12,43","3,22","1,61","3,79","9,63",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","39,1","0,45","7246,9/5209,1","12,43","3,22","1,61","4,05","10,30",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,110,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","37,6","0,45","7414,9/5388,7","12,43","3,22","1,61","4,33","11,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","250,9","0,45","723,8/206,3","10,82","3,24","1,85","0,01","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","186,0","0,45","1180,0/412,6","10,82","3,24","1,85","0,04","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","153,8","0,45","1570,5/618,9","10,82","3,24","1,85","0,08","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","133,1","0,45","1923,3/825,2","10,82","3,24","1,85","0,14","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","118,2","0,45","2250,3/1031,5","10,82","3,24","1,85","0,21","0,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","106,7","0,45","2558,0/1237,8","10,82","3,24","1,85","0,29","0,56",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","97,4","0,45","2850,4/1444,1","10,82","3,24","1,85","0,39","0,75",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","89,7","0,45","3130,2/1650,4","10,82","3,24","1,85","0,50","0,95",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","83,1","0,45","3399,4/1856,6","10,82","3,24","1,85","0,62","1,18",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","77,4","0,45","3659,4/2062,9","10,82","3,24","1,85","0,75","1,43",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","72,4","0,45","3911,5/2269,2","10,82","3,24","1,85","0,89","1,71",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","67,9","0,45","4156,4/2475,5","10,82","3,24","1,85","1,04","2,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,9","0,45","4394,9/2681,8","10,82","3,24","1,85","1,21","2,32",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","60,2","0,45","4627,7/2888,1","10,82","3,24","1,85","1,38","2,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","57,0","0,45","4857,2/3094,4","10,82","3,24","1,85","1,57","3,01",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","54,1","0,45","5084,9/3300,7","10,82","3,24","1,85","1,76","3,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","51,5","0,45","5313,3/3507,0","10,82","3,24","1,85","1,97","3,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","49,1","0,45","5536,1/3713,3","10,82","3,24","1,85","2,19","4,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","46,9","0,45","5758,1/3919,6","10,82","3,24","1,85","2,41","4,55",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","44,7","0,45","5969,5/4125,9","10,82","3,24","1,85","2,65","5,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","42,6","0,45","6178,8/4332,2","10,82","3,24","1,85","2,90","5,52",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","40,7","0,45","6386,9/4538,5","10,82","3,24","1,85","3,08","6,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","38,8","0,45","6584,2/4744,8","10,82","3,24","1,85","3,36","6,58",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","37,1","0,45","6789,9/4951,1","10,82","3,24","1,85","3,65","7,15",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","35,4","0,45","6981,6/5157,3","10,82","3,24","1,85","3,94","7,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","33,7","0,45","7170,7/5363,6","10,82","3,24","1,85","4,25","8,34",{"$f":"AND(N390=$AZ$4,X390=$BA$4,AD390=$BB$4)","v":false},{"$f":"AX390*AV390","v":0},{"$f":"AX390*AW390","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","32,1","0,45","7357,3/5569,9","10,82","3,24","1,85","4,58","8,97",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","30,6","0,45","7541,6/5776,2","10,82","3,24","1,85","4,91","9,63",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","29,1","0,45","7723,6/5982,5","10,82","3,24","1,85","5,25","10,30",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,105,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","27,7","0,45","7903,5/6188,8","10,82","3,24","1,85","5,61","11,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","215,2","0,45","772,9/245,2","9,10","3,30","2,20","0,01","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","157,4","0,45","1262,2/490,5","9,10","3,30","2,20","0,05","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","128,6","0,45","1681,7/735,7","9,10","3,30","2,20","0,11","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","110,1","0,45","2061,2/980,9","9,10","3,30","2,20","0,19","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","96,8","0,45","2413,4/1226,1","9,10","3,30","2,20","0,28","0,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","86,6","0,45","2744,9/1471,4","9,10","3,30","2,20","0,39","0,56",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","78,3","0,45","3060,3/1716,6","9,10","3,30","2,20","0,52","0,75",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","71,4","0,45","3362,2/1961,8","9,10","3,30","2,20","0,66","0,95",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","65,5","0,45","3652,9/2207,0","9,10","3,30","2,20","0,82","1,18",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","60,4","0,45","3933,9/2452,3","9,10","3,30","2,20","0,99","1,43",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","55,9","0,45","4206,3/2697,5","9,10","3,30","2,20","1,18","1,71",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","51,9","0,45","4471,2/2942,7","9,10","3,30","2,20","1,39","2,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","48,3","0,45","4729,3/3187,9","9,10","3,30","2,20","1,61","2,32",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","45,1","0,45","4981,2/3433,2","9,10","3,30","2,20","1,84","2,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","42,3","0,45","5233,7/3678,4","9,10","3,30","2,20","2,09","3,01",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","39,8","0,45","5486,4/3923,6","9,10","3,30","2,20","2,35","3,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","37,5","0,45","5732,8/4168,8","9,10","3,30","2,20","2,62","3,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","35,4","0,45","5977,5/4414,1","9,10","3,30","2,20","2,91","4,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","33,5","0,45","6222,2/4659,3","9,10","3,30","2,20","3,13","4,55",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","31,4","0,45","6446,6/4904,5","9,10","3,30","2,20","3,46","5,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","29,7","0,45","6677,9/5149,7","9,10","3,30","2,20","3,80","5,52",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","27,8","0,45","6895,2/5395,0","9,10","3,30","2,20","4,16","6,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","26,0","0,45","7109,3/5640,2","9,10","3,30","2,20","4,53","6,58",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","24,4","0,45","7320,4/5885,4","9,10","3,30","2,20","4,92","7,15",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","22,8","0,45","7528,6/6130,6","9,10","3,30","2,20","5,32","7,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","21,3","0,45","7734,0/6375,9","9,10","3,30","2,20","5,74","8,34",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","19,9","0,45","7936,8/6621,1","9,10","3,30","2,20","6,17","8,97",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","18,5","0,45","8137,1/6866,3","9,10","3,30","2,20","6,62","9,63",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","17,2","0,45","8335,0/7111,6","9,10","3,30","2,20","7,09","10,30",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,100,70,null,null,null,65,85,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","16,0","0,45","8530,7/7356,8","9,10","3,30","2,20","7,56","11,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","371,5","0,45","538,6/114,2","19,54","3,34","1,02","0,00","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","283,3","0,45","875,5/228,4","19,54","3,34","1,02","0,01","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","239,4","0,45","1163,1/342,6","19,54","3,34","1,02","0,03","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","211,3","0,45","1422,4/456,9","19,54","3,34","1,02","0,04","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","191,1","0,45","1662,3/571,1","19,54","3,34","1,02","0,07","0,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","175,5","0,45","1887,9/685,3","19,54","3,34","1,02","0,09","0,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","162,9","0,45","2101,9/799,5","19,54","3,34","1,02","0,12","0,75",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","152,4","0,45","2306,6/913,7","19,54","3,34","1,02","0,16","0,96",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","143,5","0,45","2503,4/1027,9","19,54","3,34","1,02","0,19","1,19",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","135,8","0,45","2693,4/1142,2","19,54","3,34","1,02","0,24","1,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","129,0","0,45","2877,3/1256,4","19,54","3,34","1,02","0,28","1,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","123,0","0,45","3056,0/1370,6","19,54","3,34","1,02","0,33","2,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","117,5","0,45","3230,0/1484,8","19,54","3,34","1,02","0,38","2,34",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","112,6","0,45","3399,6/1599,0","19,54","3,34","1,02","0,44","2,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","108,1","0,45","3565,4/1713,2","19,54","3,34","1,02","0,50","3,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","104,1","0,45","3729,0/1827,4","19,54","3,34","1,02","0,56","3,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","100,3","0,45","3890,0/1941,7","19,54","3,34","1,02","0,62","3,82",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","97,0","0,45","4049,1/2055,9","19,54","3,34","1,02","0,69","4,24",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","93,8","0,45","4205,7/2170,1","19,54","3,34","1,02","0,76","4,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","91,0","0,45","4363,3/2284,3","19,54","3,34","1,02","0,84","5,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","88,1","0,45","4511,1/2398,5","19,54","3,34","1,02","0,92","5,54",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","85,3","0,45","4656,6/2512,7","19,54","3,34","1,02","1,00","6,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","82,7","0,45","4799,8/2627,0","19,54","3,34","1,02","1,08","6,60",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","80,2","0,45","4941,0/2741,2","19,54","3,34","1,02","1,17","7,17",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","78,0","0,45","5081,2/2855,4","19,54","3,34","1,02","1,26","7,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","75,8","0,45","5219,6/2969,6","19,54","3,34","1,02","1,35","8,37",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,7","0,45","5356,5/3083,8","19,54","3,34","1,02","1,45","9,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","71,7","0,45","5490,1/3198,0","19,54","3,34","1,02","1,55","9,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","69,8","0,45","5623,8/3312,3","19,54","3,34","1,02","1,65","10,33",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,130,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","68,0","0,45","5756,0/3426,5","19,54","3,34","1,02","1,76","11,03",{"$f":"AND(N454=$AZ$4,X454=$BA$4,AD454=$BB$4)","v":false},{"$f":"AX454*AV454","v":0},{"$f":"AX454*AW454","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","355,8","0,45","558,9/122,6","18,20","3,30","1,10","0,00","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","270,6","0,45","908,9/245,2","18,20","3,30","1,10","0,01","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","228,3","0,45","1207,5/367,8","18,20","3,30","1,10","0,03","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","201,1","0,45","1476,9/490,5","18,20","3,30","1,10","0,05","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","181,6","0,45","1726,3/613,1","18,20","3,30","1,10","0,08","0,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","166,5","0,45","1960,6/735,7","18,20","3,30","1,10","0,11","0,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","154,4","0,45","2183,1/858,3","18,20","3,30","1,10","0,14","0,75",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","144,3","0,45","2395,9/980,9","18,20","3,30","1,10","0,18","0,96",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","135,6","0,45","2600,4/1103,5","18,20","3,30","1,10","0,23","1,19",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","128,2","0,45","2797,8/1226,1","18,20","3,30","1,10","0,27","1,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","121,6","0,45","2989,1/1348,7","18,20","3,30","1,10","0,33","1,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","115,8","0,45","3174,8/1471,4","18,20","3,30","1,10","0,38","2,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","110,5","0,45","3355,6/1594,0","18,20","3,30","1,10","0,44","2,34",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","105,8","0,45","3532,0/1716,6","18,20","3,30","1,10","0,51","2,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","101,4","0,45","3704,3/1839,2","18,20","3,30","1,10","0,58","3,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","97,5","0,45","3874,7/1961,8","18,20","3,30","1,10","0,65","3,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","93,9","0,45","4041,5/2084,4","18,20","3,30","1,10","0,72","3,82",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","90,6","0,45","4207,1/2207,0","18,20","3,30","1,10","0,80","4,24",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","87,6","0,45","4370,2/2329,6","18,20","3,30","1,10","0,89","4,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","84,9","0,45","4534,4/2452,3","18,20","3,30","1,10","0,97","5,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","82,1","0,45","4688,1/2574,9","18,20","3,30","1,10","1,07","5,54",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","79,4","0,45","4839,4/2697,5","18,20","3,30","1,10","1,16","6,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","76,9","0,45","4988,3/2820,1","18,20","3,30","1,10","1,26","6,60",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","74,5","0,45","5136,3/2942,7","18,20","3,30","1,10","1,36","7,17",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","72,3","0,45","5282,4/3065,3","18,20","3,30","1,10","1,46","7,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","70,2","0,45","5426,7/3187,9","18,20","3,30","1,10","1,57","8,37",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","68,2","0,45","5567,5/3310,6","18,20","3,30","1,10","1,69","9,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","66,3","0,45","5708,4/3433,2","18,20","3,30","1,10","1,80","9,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","64,5","0,45","5847,8/3555,8","18,20","3,30","1,10","1,92","10,33",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,125,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","62,7","0,45","5983,5/3678,4","18,20","3,30","1,10","2,04","11,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","338,6","0,45","581,6/132,6","16,83","3,27","1,19","0,00","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","256,7","0,45","946,0/265,2","16,83","3,27","1,19","0,02","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","216,0","0,45","1257,2/397,9","16,83","3,27","1,19","0,04","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","189,9","0,45","1537,9/530,5","16,83","3,27","1,19","0,06","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","171,1","0,45","1797,7/663,1","16,83","3,27","1,19","0,09","0,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","156,6","0,45","2042,0/795,7","16,83","3,27","1,19","0,13","0,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","144,9","0,45","2273,9/928,3","16,83","3,27","1,19","0,17","0,75",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","135,2","0,45","2495,7/1060,9","16,83","3,27","1,19","0,22","0,96",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","127,0","0,45","2708,9/1193,6","16,83","3,27","1,19","0,27","1,19",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","119,8","0,45","2914,8/1326,2","16,83","3,27","1,19","0,32","1,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","113,5","0,45","3114,2/1458,8","16,83","3,27","1,19","0,39","1,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","107,9","0,45","3307,9/1591,4","16,83","3,27","1,19","0,45","2,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","102,8","0,45","3496,4/1724,0","16,83","3,27","1,19","0,52","2,34",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","98,2","0,45","3680,4/1856,6","16,83","3,27","1,19","0,60","2,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","94,0","0,45","3860,1/1989,3","16,83","3,27","1,19","0,68","3,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","90,3","0,45","4037,4/2121,9","16,83","3,27","1,19","0,76","3,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","86,9","0,45","4212,6/2254,5","16,83","3,27","1,19","0,85","3,82",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","83,7","0,45","4384,4/2387,1","16,83","3,27","1,19","0,95","4,24",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","80,8","0,45","4554,8/2519,7","16,83","3,27","1,19","1,05","4,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","78,2","0,45","4726,5/2652,3","16,83","3,27","1,19","1,15","5,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","75,5","0,45","4886,9/2785,0","16,83","3,27","1,19","1,25","5,54",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","72,9","0,45","5044,7/2917,6","16,83","3,27","1,19","1,37","6,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","70,5","0,45","5201,5/3050,2","16,83","3,27","1,19","1,48","6,60",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","68,3","0,45","5356,2/3182,8","16,83","3,27","1,19","1,60","7,17",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","66,2","0,45","5508,9/3315,4","16,83","3,27","1,19","1,73","7,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","64,1","0,45","5657,8/3448,1","16,83","3,27","1,19","1,85","8,37",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","62,2","0,45","5806,9/3580,7","16,83","3,27","1,19","1,99","9,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","60,4","0,45","5954,5/3713,3","16,83","3,27","1,19","2,12","9,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","58,6","0,45","6097,7/3845,9","16,83","3,27","1,19","2,26","10,33",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,120,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","56,9","0,45","6242,3/3978,5","16,83","3,27","1,19","2,41","11,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","319,3","0,45","607,1/144,8","15,42","3,25","1,30","0,01","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","241,1","0,45","987,9/289,6","15,42","3,25","1,30","0,02","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","202,3","0,45","1313,1/434,4","15,42","3,25","1,30","0,04","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","177,4","0,45","1606,6/579,1","15,42","3,25","1,30","0,07","0,27",{"$f":"AND(N518=$AZ$4,X518=$BA$4,AD518=$BB$4)","v":false},{"$f":"AX518*AV518","v":0},{"$f":"AX518*AW518","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","159,5","0,45","1878,4/723,9","15,42","3,25","1,30","0,11","0,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","145,6","0,45","2133,9/868,7","15,42","3,25","1,30","0,15","0,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","134,5","0,45","2376,6/1013,5","15,42","3,25","1,30","0,20","0,75",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","125,2","0,45","2608,6/1158,3","15,42","3,25","1,30","0,26","0,96",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","117,3","0,45","2831,8/1303,1","15,42","3,25","1,30","0,32","1,19",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","110,5","0,45","3047,2/1447,8","15,42","3,25","1,30","0,39","1,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","104,4","0,45","3256,0/1592,6","15,42","3,25","1,30","0,46","1,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","99,1","0,45","3458,7/1737,4","15,42","3,25","1,30","0,54","2,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","94,2","0,45","3656,1/1882,2","15,42","3,25","1,30","0,63","2,34",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","89,9","0,45","3848,7/2027,0","15,42","3,25","1,30","0,72","2,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","85,9","0,45","4036,9/2171,8","15,42","3,25","1,30","0,81","3,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","82,3","0,45","4222,8/2316,6","15,42","3,25","1,30","0,91","3,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","79,0","0,45","4405,5/2461,3","15,42","3,25","1,30","1,02","3,82",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","76,0","0,45","4587,9/2606,1","15,42","3,25","1,30","1,13","4,24",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,2","0,45","4764,4/2750,9","15,42","3,25","1,30","1,25","4,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","70,8","0,45","4944,8/2895,7","15,42","3,25","1,30","1,37","5,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","68,2","0,45","5112,8/3040,5","15,42","3,25","1,30","1,50","5,54",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","65,8","0,45","5279,7/3185,3","15,42","3,25","1,30","1,63","6,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,5","0,45","5444,3/3330,1","15,42","3,25","1,30","1,77","6,60",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","61,4","0,45","5606,8/3474,8","15,42","3,25","1,30","1,92","7,17",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","59,3","0,45","5767,5/3619,6","15,42","3,25","1,30","2,06","7,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","57,4","0,45","5923,5/3764,4","15,42","3,25","1,30","2,22","8,37",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","55,5","0,45","6080,4/3909,2","15,42","3,25","1,30","2,38","9,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","53,8","0,45","6236,1/4054,0","15,42","3,25","1,30","2,54","9,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","52,1","0,45","6386,2/4198,8","15,42","3,25","1,30","2,71","10,33",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,115,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","50,5","0,45","6539,2/4343,5","15,42","3,25","1,30","2,81","11,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","297,6","0,45","636,1/160,0","13,95","3,23","1,43","0,01","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","223,7","0,45","1035,6/320,0","13,95","3,23","1,43","0,02","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","186,9","0,45","1377,1/479,9","13,95","3,23","1,43","0,05","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","163,4","0,45","1685,3/639,9","13,95","3,23","1,43","0,09","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","146,4","0,45","1970,8/799,9","13,95","3,23","1,43","0,13","0,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","133,3","0,45","2239,3/959,9","13,95","3,23","1,43","0,19","0,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","122,7","0,45","2494,4/1119,8","13,95","3,23","1,43","0,25","0,75",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","114,0","0,45","2738,3/1279,8","13,95","3,23","1,43","0,31","0,96",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","106,5","0,45","2972,9/1439,8","13,95","3,23","1,43","0,39","1,19",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","100,0","0,45","3199,5/1599,8","13,95","3,23","1,43","0,47","1,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","94,3","0,45","3419,0/1759,8","13,95","3,23","1,43","0,56","1,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","89,2","0,45","3632,3/1919,7","13,95","3,23","1,43","0,66","2,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","84,6","0,45","3840,0/2079,7","13,95","3,23","1,43","0,76","2,34",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","80,5","0,45","4042,6/2239,7","13,95","3,23","1,43","0,87","2,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","76,7","0,45","4240,6/2399,7","13,95","3,23","1,43","0,99","3,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,3","0,45","4436,6/2559,7","13,95","3,23","1,43","1,11","3,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","70,2","0,45","4629,6/2719,6","13,95","3,23","1,43","1,24","3,82",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","67,4","0,45","4820,3/2879,6","13,95","3,23","1,43","1,38","4,24",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","64,8","0,45","5010,7/3039,6","13,95","3,23","1,43","1,52","4,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","62,4","0,45","5196,8/3199,6","13,95","3,23","1,43","1,67","5,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","60,0","0,45","5375,5/3359,5","13,95","3,23","1,43","1,83","5,54",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","57,7","0,45","5551,7/3519,5","13,95","3,23","1,43","1,99","6,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","55,6","0,45","5725,7/3679,5","13,95","3,23","1,43","2,16","6,60",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","53,6","0,45","5897,6/3839,5","13,95","3,23","1,43","2,33","7,17",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","51,6","0,45","6064,1/3999,5","13,95","3,23","1,43","2,51","7,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","49,8","0,45","6232,1/4159,4","13,95","3,23","1,43","2,70","8,37",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","48,1","0,45","6398,9/4319,4","13,95","3,23","1,43","2,89","9,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","46,4","0,45","6559,0/4479,4","13,95","3,23","1,43","3,02","9,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","44,9","0,45","6723,1/4639,4","13,95","3,23","1,43","3,23","10,33",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,110,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","43,3","0,45","6879,4/4799,4","13,95","3,23","1,43","3,45","11,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","272,8","0,45","669,6/179,6","12,43","3,22","1,61","0,01","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","203,7","0,45","1090,9/359,2","12,43","3,22","1,61","0,03","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","169,3","0,45","1451,4/538,9","12,43","3,22","1,61","0,07","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","147,3","0,45","1776,9/718,5","12,43","3,22","1,61","0,11","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","131,4","0,45","2078,6/898,1","12,43","3,22","1,61","0,17","0,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","119,2","0,45","2362,4/1077,7","12,43","3,22","1,61","0,23","0,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","109,3","0,45","2632,1/1257,4","12,43","3,22","1,61","0,31","0,75",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","101,1","0,45","2890,1/1437,0","12,43","3,22","1,61","0,39","0,96",{"$f":"AND(N582=$AZ$4,X582=$BA$4,AD582=$BB$4)","v":false},{"$f":"AX582*AV582","v":0},{"$f":"AX582*AW582","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","94,1","0,45","3138,3/1616,6","12,43","3,22","1,61","0,48","1,19",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","88,1","0,45","3378,0/1796,2","12,43","3,22","1,61","0,59","1,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","82,7","0,45","3610,3/1975,9","12,43","3,22","1,61","0,70","1,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","78,0","0,45","3836,1/2155,5","12,43","3,22","1,61","0,82","2,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,7","0,45","4055,9/2335,1","12,43","3,22","1,61","0,95","2,34",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","69,8","0,45","4270,5/2514,7","12,43","3,22","1,61","1,09","2,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","66,3","0,45","4480,2/2694,4","12,43","3,22","1,61","1,23","3,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,1","0,45","4688,5/2874,0","12,43","3,22","1,61","1,39","3,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","60,3","0,45","4893,9/3053,6","12,43","3,22","1,61","1,55","3,82",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","57,6","0,45","5094,1/3233,2","12,43","3,22","1,61","1,72","4,24",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","55,3","0,45","5298,6/3412,9","12,43","3,22","1,61","1,90","4,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","53,1","0,45","5498,8/3592,5","12,43","3,22","1,61","2,08","5,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","50,7","0,45","5686,3/3772,1","12,43","3,22","1,61","2,28","5,54",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","48,6","0,45","5873,9/3951,7","12,43","3,22","1,61","2,48","6,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","46,7","0,45","6059,3/4131,4","12,43","3,22","1,61","2,69","6,60",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","44,8","0,45","6243,0/4311,0","12,43","3,22","1,61","2,91","7,17",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","43,0","0,45","6419,6/4490,6","12,43","3,22","1,61","3,13","7,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","41,3","0,45","6599,9/4670,2","12,43","3,22","1,61","3,29","8,37",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","39,8","0,45","6780,0/4849,9","12,43","3,22","1,61","3,54","9,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","38,2","0,45","6949,9/5029,5","12,43","3,22","1,61","3,80","9,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","36,9","0,45","7129,9/5209,1","12,43","3,22","1,61","4,06","10,33",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,105,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","35,4","0,45","7295,7/5388,7","12,43","3,22","1,61","4,34","11,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","243,7","0,45","709,1/206,3","10,82","3,24","1,85","0,01","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","180,3","0,45","1156,7/412,6","10,82","3,24","1,85","0,04","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","148,8","0,45","1539,9/618,9","10,82","3,24","1,85","0,08","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","128,6","0,45","1886,4/825,2","10,82","3,24","1,85","0,14","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","114,0","0,45","2207,6/1031,5","10,82","3,24","1,85","0,21","0,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","102,8","0,45","2510,0/1237,8","10,82","3,24","1,85","0,30","0,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","93,7","0,45","2797,4/1444,1","10,82","3,24","1,85","0,39","0,75",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","86,2","0,45","3072,5/1650,4","10,82","3,24","1,85","0,50","0,96",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","79,7","0,45","3337,3/1856,6","10,82","3,24","1,85","0,62","1,19",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","74,2","0,45","3593,1/2062,9","10,82","3,24","1,85","0,75","1,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","69,3","0,45","3841,1/2269,2","10,82","3,24","1,85","0,90","1,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","64,9","0,45","4082,2/2475,5","10,82","3,24","1,85","1,05","2,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","61,0","0,45","4317,1/2681,8","10,82","3,24","1,85","1,22","2,34",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","57,4","0,45","4546,3/2888,1","10,82","3,24","1,85","1,39","2,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","54,2","0,45","4770,4/3094,4","10,82","3,24","1,85","1,58","3,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","51,3","0,45","4994,1/3300,7","10,82","3,24","1,85","1,78","3,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","48,6","0,45","5211,9/3507,0","10,82","3,24","1,85","1,99","3,82",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","46,3","0,45","5433,2/3713,3","10,82","3,24","1,85","2,21","4,24",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","44,1","0,45","5649,3/3919,6","10,82","3,24","1,85","2,43","4,68",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","42,2","0,45","5865,0/4125,9","10,82","3,24","1,85","2,67","5,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","40,1","0,45","6070,2/4332,2","10,82","3,24","1,85","2,92","5,54",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","38,2","0,45","6273,7/4538,5","10,82","3,24","1,85","3,18","6,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","36,3","0,45","6468,2/4744,8","10,82","3,24","1,85","3,37","6,60",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","34,7","0,45","6668,0/4951,1","10,82","3,24","1,85","3,66","7,17",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","33,0","0,45","6857,1/5157,3","10,82","3,24","1,85","3,96","7,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","31,5","0,45","7055,4/5363,6","10,82","3,24","1,85","4,27","8,37",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","30,0","0,45","7239,6/5569,9","10,82","3,24","1,85","4,59","9,00",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","28,5","0,45","7421,5/5776,2","10,82","3,24","1,85","4,92","9,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","27,1","0,45","7601,2/5982,5","10,82","3,24","1,85","5,27","10,33",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,100,65,null,null,null,60,80,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","25,7","0,45","7778,9/6188,8","10,82","3,24","1,85","5,62","11,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","375,8","0,45","509,3/107,0","20,85","3,37","0,96","0,00","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","286,9","0,45","828,3/214,1","20,85","3,37","0,96","0,01","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","242,7","0,45","1100,6/321,1","20,85","3,37","0,96","0,02","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","214,4","0,45","1346,2/428,2","20,85","3,37","0,96","0,04","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","194,0","0,45","1573,7/535,2","20,85","3,37","0,96","0,06","0,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","178,3","0,45","1787,4/642,3","20,85","3,37","0,96","0,08","0,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","165,6","0,45","1990,5/749,3","20,85","3,37","0,96","0,11","0,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","155,1","0,45","2184,6/856,4","20,85","3,37","0,96","0,14","0,97",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","146,1","0,45","2371,3/963,4","20,85","3,37","0,96","0,17","1,21",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","138,4","0,45","2551,6/1070,5","20,85","3,37","0,96","0,21","1,46",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","131,5","0,45","2726,2/1177,5","20,85","3,37","0,96","0,25","1,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","125,4","0,45","2895,8/1284,6","20,85","3,37","0,96","0,29","2,04",{"$f":"AND(N646=$AZ$4,X646=$BA$4,AD646=$BB$4)","v":false},{"$f":"AX646*AV646","v":0},{"$f":"AX646*AW646","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","120,0","0,45","3061,0/1391,6","20,85","3,37","0,96","0,33","2,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","115,0","0,45","3222,1/1498,7","20,85","3,37","0,96","0,38","2,71",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","110,5","0,45","3379,6/1605,7","20,85","3,37","0,96","0,43","3,07",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","106,3","0,45","3533,7/1712,8","20,85","3,37","0,96","0,49","3,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","102,5","0,45","3685,9/1819,8","20,85","3,37","0,96","0,55","3,86",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","99,1","0,45","3835,7/1926,9","20,85","3,37","0,96","0,61","4,29",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","95,8","0,45","3982,7/2033,9","20,85","3,37","0,96","0,67","4,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","92,9","0,45","4129,3/2141,0","20,85","3,37","0,96","0,73","5,20",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","90,1","0,45","4274,5/2248,0","20,85","3,37","0,96","0,80","5,56",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","87,6","0,45","4417,1/2355,1","20,85","3,37","0,96","0,87","6,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","84,9","0,45","4553,4/2462,1","20,85","3,37","0,96","0,95","6,63",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","82,5","0,45","4687,7/2569,2","20,85","3,37","0,96","1,02","7,19",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","80,1","0,45","4820,0/2676,2","20,85","3,37","0,96","1,10","7,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","77,9","0,45","4950,6/2783,3","20,85","3,37","0,96","1,19","8,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","75,8","0,45","5080,5/2890,3","20,85","3,37","0,96","1,27","9,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,8","0,45","5208,9/2997,4","20,85","3,37","0,96","1,36","9,69",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","71,9","0,45","5335,9/3104,4","20,85","3,37","0,96","1,45","10,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,130,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","70,0","0,45","5460,1/3211,5","20,85","3,37","0,96","1,54","11,07",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","361,4","0,45","527,0/114,2","19,54","3,34","1,02","0,00","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","275,2","0,45","857,0/228,4","19,54","3,34","1,02","0,01","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","232,3","0,45","1138,8/342,6","19,54","3,34","1,02","0,03","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","204,9","0,45","1393,0/456,9","19,54","3,34","1,02","0,04","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","185,1","0,45","1628,3/571,1","19,54","3,34","1,02","0,07","0,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","169,9","0,45","1849,5/685,3","19,54","3,34","1,02","0,09","0,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","157,6","0,45","2059,5/799,5","19,54","3,34","1,02","0,12","0,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","147,4","0,45","2260,4/913,7","19,54","3,34","1,02","0,16","0,97",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","138,7","0,45","2453,6/1027,9","19,54","3,34","1,02","0,20","1,21",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","131,1","0,45","2640,1/1142,2","19,54","3,34","1,02","0,24","1,46",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","124,5","0,45","2820,7/1256,4","19,54","3,34","1,02","0,28","1,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","118,6","0,45","2996,2/1370,6","19,54","3,34","1,02","0,33","2,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","113,3","0,45","3167,1/1484,8","19,54","3,34","1,02","0,38","2,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","108,5","0,45","3333,8/1599,0","19,54","3,34","1,02","0,44","2,71",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","104,1","0,45","3496,7/1713,2","19,54","3,34","1,02","0,50","3,07",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","100,1","0,45","3656,0/1827,4","19,54","3,34","1,02","0,56","3,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","96,4","0,45","3813,7/1941,7","19,54","3,34","1,02","0,63","3,86",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","93,0","0,45","3968,2/2055,9","19,54","3,34","1,02","0,70","4,29",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","89,9","0,45","4121,4/2170,1","19,54","3,34","1,02","0,77","4,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","87,0","0,45","4272,2/2284,3","19,54","3,34","1,02","0,84","5,20",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","84,4","0,45","4422,6/2398,5","19,54","3,34","1,02","0,92","5,56",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","81,9","0,45","4570,3/2512,7","19,54","3,34","1,02","1,01","6,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","79,3","0,45","4711,2/2627,0","19,54","3,34","1,02","1,09","6,63",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","76,9","0,45","4850,1/2741,2","19,54","3,34","1,02","1,18","7,19",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","74,7","0,45","4987,0/2855,4","19,54","3,34","1,02","1,27","7,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","72,5","0,45","5123,1/2969,6","19,54","3,34","1,02","1,36","8,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","70,5","0,45","5257,7/3083,8","19,54","3,34","1,02","1,46","9,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","68,5","0,45","5389,3/3198,0","19,54","3,34","1,02","1,56","9,69",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","66,7","0,45","5520,7/3312,3","19,54","3,34","1,02","1,67","10,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,125,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","64,9","0,45","5650,7/3426,5","19,54","3,34","1,02","1,77","11,07",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","346,0","0,45","546,9/122,6","18,20","3,30","1,10","0,00","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","262,8","0,45","889,6/245,2","18,20","3,30","1,10","0,01","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","221,4","0,45","1182,3/367,8","18,20","3,30","1,10","0,03","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","194,9","0,45","1446,4/490,5","18,20","3,30","1,10","0,05","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","175,8","0,45","1690,9/613,1","18,20","3,30","1,10","0,08","0,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","161,1","0,45","1920,8/735,7","18,20","3,30","1,10","0,11","0,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","149,2","0,45","2139,1/858,3","18,20","3,30","1,10","0,14","0,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","139,4","0,45","2347,9/980,9","18,20","3,30","1,10","0,18","0,97",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","131,0","0,45","2548,7/1103,5","18,20","3,30","1,10","0,23","1,21",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","123,7","0,45","2742,5/1226,1","18,20","3,30","1,10","0,28","1,46",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","117,3","0,45","2930,4/1348,7","18,20","3,30","1,10","0,33","1,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","111,6","0,45","3112,8/1471,4","18,20","3,30","1,10","0,39","2,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","106,4","0,45","3290,5/1594,0","18,20","3,30","1,10","0,45","2,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","101,8","0,45","3463,8/1716,6","18,20","3,30","1,10","0,51","2,71",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","97,5","0,45","3633,1/1839,2","18,20","3,30","1,10","0,58","3,07",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","93,6","0,45","3798,8/1961,8","18,20","3,30","1,10","0,65","3,45",{"$f":"AND(N710=$AZ$4,X710=$BA$4,AD710=$BB$4)","v":false},{"$f":"AX710*AV710","v":0},{"$f":"AX710*AW710","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","90,1","0,45","3962,3/2084,4","18,20","3,30","1,10","0,73","3,86",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","86,9","0,45","4124,0/2207,0","18,20","3,30","1,10","0,81","4,29",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","83,8","0,45","4282,6/2329,6","18,20","3,30","1,10","0,89","4,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","81,0","0,45","4439,5/2452,3","18,20","3,30","1,10","0,98","5,20",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","78,5","0,45","4596,2/2574,9","18,20","3,30","1,10","1,07","5,56",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","76,1","0,45","4750,0/2697,5","18,20","3,30","1,10","1,17","6,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,6","0,45","4896,6/2820,1","18,20","3,30","1,10","1,27","6,63",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","71,3","0,45","5041,0/2942,7","18,20","3,30","1,10","1,37","7,19",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","69,1","0,45","5184,7/3065,3","18,20","3,30","1,10","1,48","7,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","67,1","0,45","5326,5/3187,9","18,20","3,30","1,10","1,59","8,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","65,1","0,45","5465,2/3310,6","18,20","3,30","1,10","1,70","9,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,2","0,45","5603,7/3433,2","18,20","3,30","1,10","1,82","9,69",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","61,4","0,45","5740,7/3555,8","18,20","3,30","1,10","1,94","10,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,120,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","59,8","0,45","5876,5/3678,4","18,20","3,30","1,10","2,06","11,07",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","329,1","0,45","569,1/132,6","16,83","3,27","1,19","0,00","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","249,1","0,45","926,0/265,2","16,83","3,27","1,19","0,02","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","209,4","0,45","1230,9/397,9","16,83","3,27","1,19","0,04","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","183,9","0,45","1506,1/530,5","16,83","3,27","1,19","0,06","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","165,6","0,45","1760,9/663,1","16,83","3,27","1,19","0,09","0,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","151,4","0,45","2000,6/795,7","16,83","3,27","1,19","0,13","0,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","140,0","0,45","2228,1/928,3","16,83","3,27","1,19","0,17","0,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","130,5","0,45","2445,8/1060,9","16,83","3,27","1,19","0,22","0,97",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","122,5","0,45","2655,2/1193,6","16,83","3,27","1,19","0,27","1,21",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","115,5","0,45","2857,3/1326,2","16,83","3,27","1,19","0,33","1,46",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","109,3","0,45","3053,2/1458,8","16,83","3,27","1,19","0,39","1,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","103,8","0,45","3243,5/1591,4","16,83","3,27","1,19","0,46","2,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","98,9","0,45","3428,7/1724,0","16,83","3,27","1,19","0,53","2,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","94,4","0,45","3609,5/1856,6","16,83","3,27","1,19","0,60","2,71",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","90,3","0,45","3786,1/1989,3","16,83","3,27","1,19","0,68","3,07",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","86,6","0,45","3959,0/2121,9","16,83","3,27","1,19","0,77","3,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","83,2","0,45","4129,8/2254,5","16,83","3,27","1,19","0,86","3,86",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","80,0","0,45","4297,8/2387,1","16,83","3,27","1,19","0,96","4,29",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","77,2","0,45","4465,1/2519,7","16,83","3,27","1,19","1,05","4,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","74,5","0,45","4627,4/2652,3","16,83","3,27","1,19","1,16","5,20",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","72,0","0,45","4791,2/2785,0","16,83","3,27","1,19","1,27","5,56",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","69,7","0,45","4952,0/2917,6","16,83","3,27","1,19","1,38","6,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","67,4","0,45","5104,9/3050,2","16,83","3,27","1,19","1,49","6,63",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","65,2","0,45","5257,0/3182,8","16,83","3,27","1,19","1,62","7,19",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,1","0,45","5407,2/3315,4","16,83","3,27","1,19","1,74","7,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","61,1","0,45","5553,8/3448,1","16,83","3,27","1,19","1,87","8,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","59,2","0,45","5700,3/3580,7","16,83","3,27","1,19","2,00","9,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","57,4","0,45","5845,3/3713,3","16,83","3,27","1,19","2,14","9,69",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","55,7","0,45","5989,0/3845,9","16,83","3,27","1,19","2,28","10,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,115,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","54,0","0,45","6128,4/3978,5","16,83","3,27","1,19","2,43","11,07",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","310,2","0,45","594,0/144,8","15,42","3,25","1,30","0,01","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","233,9","0,45","966,9/289,6","15,42","3,25","1,30","0,02","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","196,0","0,45","1285,7/434,4","15,42","3,25","1,30","0,04","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","171,7","0,45","1573,5/579,1","15,42","3,25","1,30","0,07","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","154,2","0,45","1840,0/723,9","15,42","3,25","1,30","0,11","0,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","140,7","0,45","2090,7/868,7","15,42","3,25","1,30","0,15","0,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","129,8","0,45","2328,9/1013,5","15,42","3,25","1,30","0,20","0,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","120,7","0,45","2556,7/1158,3","15,42","3,25","1,30","0,26","0,97",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","113,0","0,45","2775,8/1303,1","15,42","3,25","1,30","0,32","1,21",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","106,3","0,45","2987,4/1447,8","15,42","3,25","1,30","0,39","1,46",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","100,4","0,45","3192,4/1592,6","15,42","3,25","1,30","0,46","1,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","95,2","0,45","3391,6/1737,4","15,42","3,25","1,30","0,54","2,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","90,5","0,45","3585,6/1882,2","15,42","3,25","1,30","0,63","2,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","86,2","0,45","3774,9/2027,0","15,42","3,25","1,30","0,72","2,71",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","82,3","0,45","3959,9/2171,8","15,42","3,25","1,30","0,82","3,07",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","78,8","0,45","4140,9/2316,6","15,42","3,25","1,30","0,92","3,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","75,5","0,45","4320,2/2461,3","15,42","3,25","1,30","1,03","3,86",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","72,5","0,45","4496,6/2606,1","15,42","3,25","1,30","1,14","4,29",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","69,8","0,45","4670,8/2750,9","15,42","3,25","1,30","1,26","4,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","67,3","0,45","4843,9/2895,7","15,42","3,25","1,30","1,39","5,20",{"$f":"AND(N774=$AZ$4,X774=$BA$4,AD774=$BB$4)","v":false},{"$f":"AX774*AV774","v":0},{"$f":"AX774*AW774","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","64,9","0,45","5013,0/3040,5","15,42","3,25","1,30","1,51","5,56",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","62,7","0,45","5181,7/3185,3","15,42","3,25","1,30","1,65","6,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","60,5","0,45","5343,5/3330,1","15,42","3,25","1,30","1,79","6,63",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","58,4","0,45","5503,3/3474,8","15,42","3,25","1,30","1,93","7,19",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","56,4","0,45","5661,2/3619,6","15,42","3,25","1,30","2,08","7,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","54,5","0,45","5814,8/3764,4","15,42","3,25","1,30","2,24","8,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","52,7","0,45","5969,0/3909,2","15,42","3,25","1,30","2,40","9,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","51,0","0,45","6121,7/4054,0","15,42","3,25","1,30","2,56","9,69",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","49,3","0,45","6269,6/4198,8","15,42","3,25","1,30","2,73","10,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,110,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","47,8","0,45","6419,5/4343,5","15,42","3,25","1,30","2,90","11,07",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","289,0","0,45","622,3/160,0","13,95","3,23","1,43","0,01","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","216,8","0,45","1013,7/320,0","13,95","3,23","1,43","0,03","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","180,9","0,45","1348,4/479,9","13,95","3,23","1,43","0,05","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","157,9","0,45","1650,6/639,9","13,95","3,23","1,43","0,09","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","141,4","0,45","1930,7/799,9","13,95","3,23","1,43","0,13","0,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","128,6","0,45","2194,1/959,9","13,95","3,23","1,43","0,19","0,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","118,3","0,45","2444,5/1119,8","13,95","3,23","1,43","0,25","0,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","109,7","0,45","2684,0/1279,8","13,95","3,23","1,43","0,32","0,97",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","102,4","0,45","2914,4/1439,8","13,95","3,23","1,43","0,39","1,21",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","96,1","0,45","3137,0/1599,8","13,95","3,23","1,43","0,48","1,46",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","90,5","0,45","3352,6/1759,8","13,95","3,23","1,43","0,57","1,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","85,6","0,45","3562,2/1919,7","13,95","3,23","1,43","0,66","2,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","81,1","0,45","3766,4/2079,7","13,95","3,23","1,43","0,77","2,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","77,1","0,45","3965,5/2239,7","13,95","3,23","1,43","0,88","2,71",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,4","0,45","4160,2/2399,7","13,95","3,23","1,43","1,00","3,07",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","70,0","0,45","4350,8/2559,7","13,95","3,23","1,43","1,12","3,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","66,9","0,45","4539,9/2719,6","13,95","3,23","1,43","1,25","3,86",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","64,1","0,45","4726,3/2879,6","13,95","3,23","1,43","1,39","4,29",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","61,5","0,45","4908,3/3039,6","13,95","3,23","1,43","1,54","4,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","59,1","0,45","5091,0/3199,6","13,95","3,23","1,43","1,69","5,20",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","56,8","0,45","5269,4/3359,5","13,95","3,23","1,43","1,84","5,56",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","54,8","0,45","5449,2/3519,5","13,95","3,23","1,43","2,01","6,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","52,7","0,45","5620,1/3679,5","13,95","3,23","1,43","2,18","6,63",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","50,8","0,45","5789,0/3839,5","13,95","3,23","1,43","2,35","7,19",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","48,8","0,45","5953,1/3999,5","13,95","3,23","1,43","2,54","7,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","47,1","0,45","6117,9/4159,4","13,95","3,23","1,43","2,73","8,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","45,4","0,45","6281,4/4319,4","13,95","3,23","1,43","2,92","9,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","43,8","0,45","6439,2/4479,4","13,95","3,23","1,43","3,12","9,69",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","42,3","0,45","6599,7/4639,4","13,95","3,23","1,43","3,33","10,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,105,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","40,7","0,45","6753,8/4799,4","13,95","3,23","1,43","3,46","11,07",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","264,7","0,45","655,1/179,6","12,43","3,22","1,61","0,01","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","197,3","0,45","1067,9/359,2","12,43","3,22","1,61","0,03","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","163,7","0,45","1421,2/538,9","12,43","3,22","1,61","0,07","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","142,2","0,45","1740,5/718,5","12,43","3,22","1,61","0,11","0,27",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","126,7","0,45","2036,5/898,1","12,43","3,22","1,61","0,17","0,41",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","114,8","0,45","2315,0/1077,7","12,43","3,22","1,61","0,23","0,57",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","105,2","0,45","2579,7/1257,4","12,43","3,22","1,61","0,31","0,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","97,2","0,45","2833,1/1437,0","12,43","3,22","1,61","0,39","0,97",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","90,3","0,45","3076,9/1616,6","12,43","3,22","1,61","0,49","1,21",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","84,4","0,45","3312,4/1796,2","12,43","3,22","1,61","0,59","1,46",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","79,2","0,45","3540,8/1975,9","12,43","3,22","1,61","0,71","1,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","74,6","0,45","3762,7/2155,5","12,43","3,22","1,61","0,83","2,04",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","70,4","0,45","3978,9/2335,1","12,43","3,22","1,61","0,96","2,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","66,6","0,45","4189,8/2514,7","12,43","3,22","1,61","1,10","2,71",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,2","0,45","4396,1/2694,4","12,43","3,22","1,61","1,24","3,07",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","60,0","0,45","4598,0/2874,0","12,43","3,22","1,61","1,40","3,45",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","57,2","0,45","4799,1/3053,6","12,43","3,22","1,61","1,56","3,86",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","54,5","0,45","4995,2/3233,2","12,43","3,22","1,61","1,74","4,29",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","52,1","0,45","5191,3/3412,9","12,43","3,22","1,61","1,92","4,73",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","49,9","0,45","5384,7/3592,5","12,43","3,22","1,61","2,10","5,20",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","47,8","0,45","5574,3/3772,1","12,43","3,22","1,61","2,30","5,56",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","45,9","0,45","5765,9/3951,7","12,43","3,22","1,61","2,50","6,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","44,0","0,45","5948,0/4131,4","12,43","3,22","1,61","2,72","6,63",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","42,2","0,45","6128,2/4311,0","12,43","3,22","1,61","2,93","7,19",{"$f":"AND(N838=$AZ$4,X838=$BA$4,AD838=$BB$4)","v":false},{"$f":"AX838*AV838","v":0},{"$f":"AX838*AW838","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","40,3","0,45","6302,2/4490,6","12,43","3,22","1,61","3,16","7,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","38,7","0,45","6478,6/4670,2","12,43","3,22","1,61","3,40","8,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","37,2","0,45","6654,2/4849,9","12,43","3,22","1,61","3,55","9,03",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","35,6","0,45","6821,6/5029,5","12,43","3,22","1,61","3,81","9,69",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","34,3","0,45","6995,4/5209,1","12,43","3,22","1,61","4,08","10,36",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,100,60,null,null,null,55,75,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","32,8","0,45","7158,9/5388,7","12,43","3,22","1,61","4,35","11,07",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","377,9","0,45","482,0/100,8","22,13","3,40","0,90","0,00","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","288,7","0,45","784,1/201,7","22,13","3,40","0,90","0,01","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","244,5","0,45","1042,2/302,5","22,13","3,40","0,90","0,02","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","216,1","0,45","1275,1/403,4","22,13","3,40","0,90","0,03","0,28",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","195,6","0,45","1490,8/504,2","22,13","3,40","0,90","0,05","0,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","179,9","0,45","1693,6/605,1","22,13","3,40","0,90","0,07","0,58",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","167,2","0,45","1886,3/705,9","22,13","3,40","0,90","0,10","0,77",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","156,6","0,45","2070,6/806,8","22,13","3,40","0,90","0,12","0,98",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","147,7","0,45","2247,9/907,6","22,13","3,40","0,90","0,15","1,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","139,9","0,45","2419,1/1008,5","22,13","3,40","0,90","0,18","1,48",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","133,0","0,45","2585,0/1109,3","22,13","3,40","0,90","0,22","1,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","126,9","0,45","2746,2/1210,2","22,13","3,40","0,90","0,26","2,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","121,4","0,45","2903,2/1311,0","22,13","3,40","0,90","0,30","2,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","116,5","0,45","3056,3/1411,9","22,13","3,40","0,90","0,34","2,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","111,9","0,45","3206,0/1512,7","22,13","3,40","0,90","0,38","3,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","107,8","0,45","3352,6/1613,6","22,13","3,40","0,90","0,43","3,49",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","103,9","0,45","3496,1/1714,4","22,13","3,40","0,90","0,48","3,90",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","100,4","0,45","3637,7/1815,3","22,13","3,40","0,90","0,54","4,33",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","97,1","0,45","3777,3/1916,1","22,13","3,40","0,90","0,59","4,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","94,1","0,45","3915,2/2017,0","22,13","3,40","0,90","0,65","5,25",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","91,3","0,45","4050,7/2117,8","22,13","3,40","0,90","0,71","5,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","88,6","0,45","4184,9/2218,7","22,13","3,40","0,90","0,77","6,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","86,2","0,45","4319,0/2319,5","22,13","3,40","0,90","0,84","6,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","83,9","0,45","4451,0/2420,4","22,13","3,40","0,90","0,91","7,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","81,5","0,45","4577,1/2521,2","22,13","3,40","0,90","0,98","7,81",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","79,3","0,45","4701,5/2622,1","22,13","3,40","0,90","1,05","8,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","77,2","0,45","4824,3/2722,9","22,13","3,40","0,90","1,12","9,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","75,1","0,45","4945,6/2823,8","22,13","3,40","0,90","1,20","9,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,2","0,45","5066,3/2924,6","22,13","3,40","0,90","1,28","10,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,130,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","71,4","0,45","5185,7/3025,5","22,13","3,40","0,90","1,36","11,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","364,9","0,45","497,7/107,0","20,85","3,37","0,96","0,00","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","278,2","0,45","809,7/214,1","20,85","3,37","0,96","0,01","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","235,1","0,45","1076,2/321,1","20,85","3,37","0,96","0,02","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","207,5","0,45","1316,7/428,2","20,85","3,37","0,96","0,04","0,28",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","187,6","0,45","1539,5/535,2","20,85","3,37","0,96","0,06","0,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","172,3","0,45","1748,9/642,3","20,85","3,37","0,96","0,08","0,58",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","159,9","0,45","1947,9/749,3","20,85","3,37","0,96","0,11","0,77",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","149,7","0,45","2138,2/856,4","20,85","3,37","0,96","0,14","0,98",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","140,9","0,45","2321,2/963,4","20,85","3,37","0,96","0,17","1,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","133,4","0,45","2498,0/1070,5","20,85","3,37","0,96","0,21","1,48",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","126,7","0,45","2669,3/1177,5","20,85","3,37","0,96","0,25","1,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","120,7","0,45","2835,7/1284,6","20,85","3,37","0,96","0,29","2,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","115,4","0,45","2997,8/1391,6","20,85","3,37","0,96","0,34","2,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","110,6","0,45","3155,9/1498,7","20,85","3,37","0,96","0,39","2,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","106,2","0,45","3310,4/1605,7","20,85","3,37","0,96","0,44","3,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","102,1","0,45","3461,7/1712,8","20,85","3,37","0,96","0,49","3,49",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","98,4","0,45","3609,9/1819,8","20,85","3,37","0,96","0,55","3,90",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","94,9","0,45","3756,1/1926,9","20,85","3,37","0,96","0,61","4,33",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","91,8","0,45","3900,5/2033,9","20,85","3,37","0,96","0,67","4,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","88,8","0,45","4042,3/2141,0","20,85","3,37","0,96","0,74","5,25",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","86,1","0,45","4183,5/2248,0","20,85","3,37","0,96","0,81","5,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","83,6","0,45","4322,9/2355,1","20,85","3,37","0,96","0,88","6,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","81,1","0,45","4459,6/2462,1","20,85","3,37","0,96","0,96","6,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","78,9","0,45","4596,0/2569,2","20,85","3,37","0,96","1,03","7,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","76,6","0,45","4726,1/2676,2","20,85","3,37","0,96","1,11","7,81",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","74,4","0,45","4854,5/2783,3","20,85","3,37","0,96","1,20","8,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","72,3","0,45","4981,3/2890,3","20,85","3,37","0,96","1,28","9,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","70,4","0,45","5107,4/2997,4","20,85","3,37","0,96","1,37","9,72",{"$f":"AND(N902=$AZ$4,X902=$BA$4,AD902=$BB$4)","v":false},{"$f":"AX902*AV902","v":0},{"$f":"AX902*AW902","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","68,5","0,45","5232,1/3104,4","20,85","3,37","0,96","1,46","10,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,125,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","66,7","0,45","5354,3/3211,5","20,85","3,37","0,96","1,55","11,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","350,8","0,45","514,9/114,2","19,54","3,34","1,02","0,00","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","266,7","0,45","837,8/228,4","19,54","3,34","1,02","0,01","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","225,0","0,45","1113,5/342,6","19,54","3,34","1,02","0,03","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","198,2","0,45","1362,4/456,9","19,54","3,34","1,02","0,05","0,28",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","178,9","0,45","1592,9/571,1","19,54","3,34","1,02","0,07","0,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","164,1","0,45","1809,6/685,3","19,54","3,34","1,02","0,09","0,58",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","152,1","0,45","2015,4/799,5","19,54","3,34","1,02","0,13","0,77",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","142,1","0,45","2212,4/913,7","19,54","3,34","1,02","0,16","0,98",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","133,6","0,45","2401,7/1027,9","19,54","3,34","1,02","0,20","1,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","126,3","0,45","2584,6/1142,2","19,54","3,34","1,02","0,24","1,48",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","119,8","0,45","2761,8/1256,4","19,54","3,34","1,02","0,29","1,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","114,1","0,45","2934,0/1370,6","19,54","3,34","1,02","0,34","2,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","108,9","0,45","3101,7/1484,8","19,54","3,34","1,02","0,39","2,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","104,2","0,45","3265,2/1599,0","19,54","3,34","1,02","0,44","2,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","99,9","0,45","3425,1/1713,2","19,54","3,34","1,02","0,50","3,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","96,0","0,45","3581,6/1827,4","19,54","3,34","1,02","0,57","3,49",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","92,4","0,45","3734,9/1941,7","19,54","3,34","1,02","0,63","3,90",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","89,0","0,45","3886,3/2055,9","19,54","3,34","1,02","0,70","4,33",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","86,0","0,45","4035,9/2170,1","19,54","3,34","1,02","0,78","4,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","83,1","0,45","4182,9/2284,3","19,54","3,34","1,02","0,85","5,25",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","80,5","0,45","4328,2/2398,5","19,54","3,34","1,02","0,93","5,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","78,0","0,45","4472,6/2512,7","19,54","3,34","1,02","1,01","6,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","75,6","0,45","4614,1/2627,0","19,54","3,34","1,02","1,10","6,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,5","0,45","4755,3/2741,2","19,54","3,34","1,02","1,19","7,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","71,3","0,45","4889,9/2855,4","19,54","3,34","1,02","1,28","7,81",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","69,1","0,45","5022,7/2969,6","19,54","3,34","1,02","1,38","8,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","67,2","0,45","5154,9/3083,8","19,54","3,34","1,02","1,47","9,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","65,3","0,45","5285,6/3198,0","19,54","3,34","1,02","1,58","9,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,4","0,45","5413,4/3312,3","19,54","3,34","1,02","1,68","10,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,120,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","61,7","0,45","5541,2/3426,5","19,54","3,34","1,02","1,79","11,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","335,8","0,45","534,4/122,6","18,20","3,30","1,10","0,00","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","254,6","0,45","869,6/245,2","18,20","3,30","1,10","0,01","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","214,3","0,45","1156,1/367,8","18,20","3,30","1,10","0,03","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","188,4","0,45","1414,7/490,5","18,20","3,30","1,10","0,05","0,28",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","169,8","0,45","1654,2/613,1","18,20","3,30","1,10","0,08","0,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","155,5","0,45","1879,4/735,7","18,20","3,30","1,10","0,11","0,58",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","143,9","0,45","2093,3/858,3","18,20","3,30","1,10","0,15","0,77",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","134,3","0,45","2298,0/980,9","18,20","3,30","1,10","0,19","0,98",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","126,1","0,45","2494,9/1103,5","18,20","3,30","1,10","0,23","1,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","119,0","0,45","2685,0/1226,1","18,20","3,30","1,10","0,28","1,48",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","112,7","0,45","2869,3/1348,7","18,20","3,30","1,10","0,33","1,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","107,2","0,45","3048,3/1471,4","18,20","3,30","1,10","0,39","2,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","102,2","0,45","3222,6/1594,0","18,20","3,30","1,10","0,45","2,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","97,6","0,45","3392,7/1716,6","18,20","3,30","1,10","0,52","2,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","93,5","0,45","3558,9/1839,2","18,20","3,30","1,10","0,59","3,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","89,7","0,45","3721,7/1961,8","18,20","3,30","1,10","0,66","3,49",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","86,2","0,45","3881,1/2084,4","18,20","3,30","1,10","0,74","3,90",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","83,0","0,45","4038,7/2207,0","18,20","3,30","1,10","0,82","4,33",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","80,0","0,45","4193,8/2329,6","18,20","3,30","1,10","0,90","4,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","77,3","0,45","4346,8/2452,3","18,20","3,30","1,10","0,99","5,25",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","74,7","0,45","4498,0/2574,9","18,20","3,30","1,10","1,08","5,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","72,3","0,45","4648,5/2697,5","18,20","3,30","1,10","1,18","6,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","70,2","0,45","4800,9/2820,1","18,20","3,30","1,10","1,28","6,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","68,0","0,45","4942,9/2942,7","18,20","3,30","1,10","1,38","7,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","65,8","0,45","5083,0/3065,3","18,20","3,30","1,10","1,49","7,81",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,8","0,45","5222,3/3187,9","18,20","3,30","1,10","1,60","8,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","61,9","0,45","5358,7/3310,6","18,20","3,30","1,10","1,72","9,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","60,0","0,45","5494,7/3433,2","18,20","3,30","1,10","1,83","9,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","58,3","0,45","5629,4/3555,8","18,20","3,30","1,10","1,95","10,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,115,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","56,7","0,45","5762,7/3678,4","18,20","3,30","1,10","2,08","11,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","319,3","0,45","556,0/132,6","16,83","3,27","1,19","0,00","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","241,3","0,45","905,2/265,2","16,83","3,27","1,19","0,02","0,08",{"$f":"AND(N966=$AZ$4,X966=$BA$4,AD966=$BB$4)","v":false},{"$f":"AX966*AV966","v":0},{"$f":"AX966*AW966","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","202,5","0,45","1203,6/397,9","16,83","3,27","1,19","0,04","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","177,7","0,45","1473,1/530,5","16,83","3,27","1,19","0,06","0,28",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","159,8","0,45","1722,7/663,1","16,83","3,27","1,19","0,09","0,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","146,0","0,45","1957,5/795,7","16,83","3,27","1,19","0,13","0,58",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","134,9","0,45","2180,5/928,3","16,83","3,27","1,19","0,17","0,77",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","125,6","0,45","2393,9/1060,9","16,83","3,27","1,19","0,22","0,98",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","117,8","0,45","2599,2/1193,6","16,83","3,27","1,19","0,27","1,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","110,9","0,45","2797,5/1326,2","16,83","3,27","1,19","0,33","1,48",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","104,9","0,45","2989,7/1458,8","16,83","3,27","1,19","0,39","1,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","99,6","0,45","3176,4/1591,4","16,83","3,27","1,19","0,46","2,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","94,8","0,45","3358,2/1724,0","16,83","3,27","1,19","0,53","2,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","90,4","0,45","3535,7/1856,6","16,83","3,27","1,19","0,61","2,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","86,5","0,45","3709,1/1989,3","16,83","3,27","1,19","0,69","3,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","82,8","0,45","3878,9/2121,9","16,83","3,27","1,19","0,78","3,49",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","79,4","0,45","4045,2/2254,5","16,83","3,27","1,19","0,87","3,90",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","76,4","0,45","4209,9/2387,1","16,83","3,27","1,19","0,96","4,33",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,5","0,45","4372,1/2519,7","16,83","3,27","1,19","1,06","4,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","70,9","0,45","4532,2/2652,3","16,83","3,27","1,19","1,17","5,25",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","68,4","0,45","4688,9/2785,0","16,83","3,27","1,19","1,28","5,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","66,1","0,45","4846,1/2917,6","16,83","3,27","1,19","1,39","6,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","64,1","0,45","5005,7/3050,2","16,83","3,27","1,19","1,51","6,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","61,9","0,45","5153,9/3182,8","16,83","3,27","1,19","1,63","7,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","59,9","0,45","5301,4/3315,4","16,83","3,27","1,19","1,76","7,81",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","57,9","0,45","5445,6/3448,1","16,83","3,27","1,19","1,89","8,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","56,1","0,45","5589,6/3580,7","16,83","3,27","1,19","2,02","9,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","54,4","0,45","5732,0/3713,3","16,83","3,27","1,19","2,16","9,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","52,7","0,45","5873,0/3845,9","16,83","3,27","1,19","2,30","10,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,110,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","51,1","0,45","6010,2/3978,5","16,83","3,27","1,19","2,45","11,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","300,8","0,45","580,4/144,8","15,42","3,25","1,30","0,01","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","226,4","0,45","945,2/289,6","15,42","3,25","1,30","0,02","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","189,4","0,45","1257,2/434,4","15,42","3,25","1,30","0,04","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","165,7","0,45","1539,0/579,1","15,42","3,25","1,30","0,07","0,28",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","148,7","0,45","1800,1/723,9","15,42","3,25","1,30","0,11","0,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","135,5","0,45","2045,8/868,7","15,42","3,25","1,30","0,16","0,58",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","124,9","0,45","2279,2/1013,5","15,42","3,25","1,30","0,21","0,77",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","116,1","0,45","2502,6/1158,3","15,42","3,25","1,30","0,26","0,98",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","108,5","0,45","2717,5/1303,1","15,42","3,25","1,30","0,33","1,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","102,0","0,45","2925,0/1447,8","15,42","3,25","1,30","0,39","1,48",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","96,3","0,45","3126,2/1592,6","15,42","3,25","1,30","0,47","1,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","91,2","0,45","3321,8/1737,4","15,42","3,25","1,30","0,55","2,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","86,6","0,45","3512,2/1882,2","15,42","3,25","1,30","0,64","2,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","82,4","0,45","3698,1/2027,0","15,42","3,25","1,30","0,73","2,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","78,6","0,45","3879,7/2171,8","15,42","3,25","1,30","0,83","3,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","75,2","0,45","4057,5/2316,6","15,42","3,25","1,30","0,93","3,49",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","71,9","0,45","4231,8/2461,3","15,42","3,25","1,30","1,04","3,90",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","69,0","0,45","4404,7/2606,1","15,42","3,25","1,30","1,15","4,33",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","66,3","0,45","4573,7/2750,9","15,42","3,25","1,30","1,27","4,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,7","0,45","4741,7/2895,7","15,42","3,25","1,30","1,40","5,25",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","61,4","0,45","4908,2/3040,5","15,42","3,25","1,30","1,53","5,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","59,2","0,45","5071,1/3185,3","15,42","3,25","1,30","1,66","6,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","57,3","0,45","5238,8/3330,1","15,42","3,25","1,30","1,80","6,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","55,3","0,45","5395,7/3474,8","15,42","3,25","1,30","1,95","7,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","53,4","0,45","5550,8/3619,6","15,42","3,25","1,30","2,10","7,81",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","51,5","0,45","5701,9/3764,4","15,42","3,25","1,30","2,26","8,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","49,7","0,45","5853,3/3909,2","15,42","3,25","1,30","2,42","9,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","48,1","0,45","6003,2/4054,0","15,42","3,25","1,30","2,58","9,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","46,4","0,45","6148,8/4198,8","15,42","3,25","1,30","2,76","10,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,105,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","44,9","0,45","6295,7/4343,5","15,42","3,25","1,30","2,93","11,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","280,1","0,45","608,1/160,0","13,95","3,23","1,43","0,01","0,02",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","209,7","0,45","990,9/320,0","13,95","3,23","1,43","0,03","0,08",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","174,7","0,45","1318,5/479,9","13,95","3,23","1,43","0,05","0,16",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","152,3","0,45","1614,5/639,9","13,95","3,23","1,43","0,09","0,28",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","136,1","0,45","1888,9/799,9","13,95","3,23","1,43","0,14","0,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,6,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","123,7","0,45","2147,1/959,9","13,95","3,23","1,43","0,19","0,58",{"$f":"AND(N1030=$AZ$4,X1030=$BA$4,AD1030=$BB$4)","v":false},{"$f":"AX1030*AV1030","v":0},{"$f":"AX1030*AW1030","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","113,6","0,45","2392,6/1119,8","13,95","3,23","1,43","0,25","0,77",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","105,3","0,45","2627,4/1279,8","13,95","3,23","1,43","0,32","0,98",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","98,2","0,45","2853,5/1439,8","13,95","3,23","1,43","0,40","1,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","92,0","0,45","3071,8/1599,8","13,95","3,23","1,43","0,48","1,48",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,11,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","86,6","0,45","3283,5/1759,8","13,95","3,23","1,43","0,57","1,76",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","81,8","0,45","3489,3/1919,7","13,95","3,23","1,43","0,67","2,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,13,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","77,4","0,45","3689,7/2079,7","13,95","3,23","1,43","0,78","2,39",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,14,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","73,5","0,45","3885,3/2239,7","13,95","3,23","1,43","0,89","2,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","69,9","0,45","4076,6/2399,7","13,95","3,23","1,43","1,01","3,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","66,6","0,45","4263,8/2559,7","13,95","3,23","1,43","1,13","3,49",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,17,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","63,5","0,45","4447,3/2719,6","13,95","3,23","1,43","1,27","3,90",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,18,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","60,7","0,45","4628,5/2879,6","13,95","3,23","1,43","1,41","4,33",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,19,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","58,2","0,45","4808,1/3039,6","13,95","3,23","1,43","1,55","4,78",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","55,8","0,45","4985,8/3199,6","13,95","3,23","1,43","1,70","5,25",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","53,6","0,45","5159,5/3359,5","13,95","3,23","1,43","1,86","5,74",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,22,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","51,5","0,45","5331,3/3519,5","13,95","3,23","1,43","2,03","6,10",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,23,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","49,8","0,45","5510,5/3679,5","13,95","3,23","1,43","2,20","6,65",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","47,8","0,45","5676,3/3839,5","13,95","3,23","1,43","2,38","7,22",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","46,0","0,45","5837,7/3999,5","13,95","3,23","1,43","2,56","7,81",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,26,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","44,2","0,45","5999,6/4159,4","13,95","3,23","1,43","2,75","8,42",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,27,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","42,6","0,45","6159,9/4319,4","13,95","3,23","1,43","2,95","9,06",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,28,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","41,0","0,45","6315,2/4479,4","13,95","3,23","1,43","3,15","9,72",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,29,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","39,5","0,45","6472,5/4639,4","13,95","3,23","1,43","3,36","10,40",false,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,30,null,"Woda",null,null,null,"Woda",null,null,null,100,55,null,null,null,50,70,null,null,null,null,null,null,0,"XB37L-1-10 G 1 (20mm)","1*4L/1*5L","B","PED Art 4.3","38,0","0,45","6624,1/4799,4","13,95","3,23","1,43","3,57","11,10",false,0,0]

{"sheet":"HEX","index":8,"n_rows":450,"n_cols":5,"rows_kept":450,"cut":false,"hidden":true,"merged":[]}
[null,"A",null,"???"]
["Typ wymiennika","Pole max. przekroju pojedyńczego\nkanału przepływowego - mm2","Pole max. przekroju pojedyńczego\nkanału przepływowego - m2","pojemność wodna na płytę","max liczba płyt"]
["XB04",34,{"$f":"B3*0.000001","v":3.4E-5},0.06,70]
["XB05M",6,6.0000000000000002E-6,0.06,70]
["XB06H+",3,3.0000000000000001E-6,1.7000000000000001E-2,70]
["XB06H",5,4.9999999999999996E-6,1.7000000000000001E-2,70]
["XB06L",9,9.0000000000000002E-6,2.5000000000000001E-2,70]
["XB10",41,4.1E-5,0.05,70]
["XB12H",4,3.9999999999999998E-6,0.05,70]
["XB12M",6,6.0000000000000002E-6,0.05,70]
["XB12L",9,9.0000000000000002E-6,0.05,70]
["XB20",41,4.1E-5,0.06,70]
["XB24",35,{"$f":"B13*0.000001","v":3.4999999999999997E-5},0.1,70]
["XB30",41,4.1E-5,7.4999999999999997E-2,100]
["XB37L",16,1.5999999999999999E-5,0.10199999999999999,120]
["XB37M",11,1.1E-5,7.0000000000000007E-2,120]
["XB37H",7,6.9999999999999999E-6,5.7000000000000002E-2,120]
["XB51L",20,1.9999999999999998E-5,0.21,120]
["XB51H",41,4.1E-5,0.21,120]
["XB52M",10,9.9999999999999991E-6,0.21,120]
["XB59",100,{"$f":"B21*0.000001","v":9.9999999999999991E-5},0.21,140]
["XB59M",9,{"$f":"B22*0.000001","v":9.0000000000000002E-6},0.21,200]
["XB60",41,4.1E-5,0.26,160]
["XB61H",6,6.0000000000000002E-6,0.153,200]
["XB61L",16,1.5999999999999999E-5,0.255,200]
["XB61M",11,1.1E-5,0.191,200]
["XB66L",18,1.8E-5,0.153,200]
["XB66H",7,6.9999999999999999E-6,0.255,200]
["XB70L",29,2.9E-5,0.7,200]
["XB70M",38,3.7999999999999995E-5,0.7,200]
["XB70H",47,4.6999999999999997E-5,0.7,200]
["XG10",41,4.1E-5,4.4999999999999998E-2,140]
["XG14H",28,2.8E-5,9.5000000000000001E-2,150]
["XG18H",28,2.8E-5,0.13,150]
["XGM032H",4,3.9999999999999998E-6,0.13,150]
["XGM032M",18,1.8E-5,0.13,150]
["XGM032L",14,1.4E-5,0.13,150]
["XG20L",39,3.8999999999999999E-5,0.48,140]
["XG20H",66,6.5999999999999992E-5,0.48,140]
["XG31L",23,2.3E-5,0.37,140]
["XG31H",49,4.8999999999999998E-5,0.37,140]
["XG30",66,6.5999999999999992E-5,1.37,270]
["XG40",119,1.1899999999999999E-4,1.37,270]
["XG50",119,1.1899999999999999E-4,1.71,220]
["XGF100-34H",38,3.7999999999999995E-5,1.71,220]
["XGF100-34M",28,2.8E-5,1.71,220]
["XGF100-34L",18,1.8E-5,1.71,220]
["XGF100-35H",78,7.7999999999999999E-5,1.71,220]
["XGF100-35M",63,6.3E-5,1.71,220]
["XGF100-35L",48,4.8000000000000001E-5,1.71,220]
["XGF100-50H",38,3.7999999999999995E-5,1.71,220]
["XGF100-50M",28,2.8E-5,1.71,220]
["XGF100-50L",18,1.8E-5,1.71,220]
["XGF100-66H",38,3.7999999999999995E-5,1.71,220]
["XGF100-66M",28,2.8E-5,1.71,220]
["XGF100-66L",18,1.8E-5,1.71,220]
["JAD 3.18",50.24,5.024E-5,0.05,120]
["JAD 5.36",50.24,5.024E-5,0.06,120]
["JAD 6.50",50.24,{"$f":"B59*0.000001","v":5.024E-5},0.06,120]
["JAD 14.163",50.24,5.024E-5,7.4999999999999997E-2,120]
["JAD 14.163.10",78.5,7.8499999999999997E-5,0.10199999999999999,120]
["JAD K 3.18",50.24,5.024E-5,7.0000000000000007E-2,120]
["JAD K 5.36",50.24,5.024E-5,5.7000000000000002E-2,120]
["JAD K 6.50",50.24,5.024E-5,0.12,120]
["JAD K 6.50.10",78.5,{"$f":"B65*0.000001","v":7.8499999999999997E-5},0.12,120]
["JAD K 14.163",50.24,5.024E-5,0.21,140]
["JAD K 14.163.10",78.5,{"$f":"B67*0.000001","v":7.8499999999999997E-5},0.21,140]
["JAD X 2.11",50.24,5.024E-5,0.26,140]
["JAD X 2.11.08.68",50.24,5.024E-5,0.7,200]
["JAD X 3.18",50.24,5.024E-5,0.7,200]
["JAD X 3.18.08.71",50.24,5.024E-5,0.7,200]
["JAD X 5.38",50.24,5.024E-5,4.4999999999999998E-2,140]
["JAD 5.38.08.71",50.24,5.024E-5,9.5000000000000001E-2,150]
["JAD X 6.50",50.24,5.024E-5,0.13,150]
["JAD X 6.50.10",78.5,7.8499999999999997E-5,0.48,140]
["JAD X 9.88",50.24,5.024E-5,0.48,140]
["JAD X 9.88.10",78.5,7.8499999999999997E-5,0.37,140]
["JAD X 12.114",50.24,5.024E-5,0.37,140]
["JAD X 12.114.10",78.5,7.8499999999999997E-5,1.37,270]
["JAD XK 2.11",50.24,5.024E-5,1.71,220]
["JAD XK 2.11.08.68",50.24,{"$f":"B81*0.000001","v":5.024E-5},0.05,120]
["JAD XK 3.18",50.24,{"$f":"B82*0.000001","v":5.024E-5},0.06,120]
["JAD XK 3.18.08.75",50.24,{"$f":"B83*0.000001","v":5.024E-5},0.06,120]
["JAD XK 5.38",50.24,{"$f":"B84*0.000001","v":5.024E-5},7.4999999999999997E-2,120]
["JAD XK 5.38.08.71",50.24,5.024E-5,0.10199999999999999,120]
["JAD XK 6.50",50.24,5.024E-5,7.0000000000000007E-2,120]
["JAD XK 6.50.10",78.5,7.8499999999999997E-5,5.7000000000000002E-2,120]
["JAD XK 6.50.08.72",50.24,5.024E-5,0.12,120]
["JAD XK 9.88",50.24,5.024E-5,0.21,140]
["JAD XK 9.88.10",78.5,7.8499999999999997E-5,0.21,140]
["JAD XK 9.88.08.65",50.24,5.024E-5,0.26,140]
["JAD XK 9.88.08.85",50.24,5.024E-5,0.7,200]
["JAD XK 12.114",50.24,5.024E-5,0.7,200]
["JAD XK 12.114.10",78.5,7.8499999999999997E-5,0.7,200]
["JAD XK 12.114.08.50",50.24,5.024E-5,4.4999999999999998E-2,140]
["JAD XK 12.114.08.60",50.24,5.024E-5,9.5000000000000001E-2,150]
["JAD XK 12.114.08.75",50.24,5.024E-5,0.13,150]
["JAD XK 17.217",50.24,5.024E-5,0.48,140]
["JAD XK 17.217.10",78.5,7.8499999999999997E-5,0.48,140]
["LA12LN",42.6,4.2599999999999999E-5,0.48,140]
["LA14LN",26.7,2.6699999999999998E-5,0.48,140]
["LA22LN",26.7,2.6699999999999998E-5,0.48,140]
["LA34LN",26.7,2.6699999999999998E-5,0.48,140]
["LB31LN",26,2.5999999999999998E-5,0.48,140]
["LB47LN",26,2.5999999999999998E-5,0.48,140]
["LA60LN",26,2.5999999999999998E-5,0.48,140]
["LC110LN",25.5,2.55E-5,0.48,140]
["LC170LN",25.5,2.55E-5,0.48,140]
["LD235LN",24.5,2.4499999999999999E-5,0.48,140]
[]
[2.5]
[3]
[3.5]
[4]
[4.5]
[5]
[]
["XB 04","XB 04"]
["XB 05M","XB 05M"]
["XB 06H+","XB 06H+"]
["XB 06H","XB 06H"]
["XB 06L","XB 06L"]
["XB 10","XB 10"]
["XB 12H","XB 12H"]
["XB 12M","XB 12M"]
["XB 12L","XB 12L"]
["XB 20","XB 20"]
["XB 24","XB 24"]
["XB 30","XB 30"]
["XB 37L","XB 37L"]
["XB 37M","XB 37M"]
["XB 37H","XB 37H"]
["XB 51L","XB 51L"]
["XB 51H","XB 51H"]
["XB 52M","XB 52M"]
["XB 59","XB 59"]
["XB 59M","XB 59M"]
["XB 60","XB 60"]
["XB 61H","XB 61H"]
["XB 61L","XB 61L"]
["XB 61M","XB 61M"]
["XB 66L","XB 66L"]
["XB 66H","XB 66H"]
["XB 70L","XB 70L"]
["XB 70M","XB 70M"]
["XB 70H","XB 70H"]
["XG 10","XG 10"]
["XG 14H","XG 14H"]
["XG 18H","XG 18H"]
["XGM 032H","XGM 032H"]
["XGM 032M","XGM 032M"]
["XGM 032L","XGM 032L"]
["XG 20L","XG 20L"]
["XG 20H","XG 20H"]
["XG 31L","XG 31L"]
["XG 31H","XG 31H"]
["XG 30","XG 30"]
["XG 40","XG 40"]
["XG 50","XG 50"]
["XGF 100-34H","XGF 100-34H"]
["XGF 100-34M","XGF 100-34M"]
["XGF 100-34L","XGF 100-34L"]
["XGF 100-35H","XGF 100-35H"]
["XGF 100-35M","XGF 100-35M"]
["XGF 100-35L","XGF 100-35L"]
["XGF 100-50H","XGF 100-50H"]
["XGF 100-50M","XGF 100-50M"]
["XGF 100-50L","XGF 100-50L"]
["XGF 100-66H","XGF 100-66H"]
["XGF 100-66M","XGF 100-66M"]
["XGF 100-66L","XGF 100-66L"]
["JAD 3.18","JAD 3.18"]
["JAD 5.36","JAD 5.36"]
["JAD 6.50","JAD 6.50"]
["JAD 14.163","JAD 14.163"]
["JAD 14.163.10","JAD 14.163.10"]
["JAD K 3.18","JAD K 3.18"]
["JAD K 5.36","JAD K 5.36"]
["JAD K 6.50","JAD K 6.50"]
["JAD K 6.50.10","JAD K 6.50"]
["JAD K 14.163","JAD K 14.163"]
["JAD K 14.163.10","JAD K 14.163.10"]
["JAD X 2.11","JAD X 2.11"]
["JAD X 2.11.08.68","JAD X 2.11.08.68"]
["JAD X 3.18","JAD X 3.18"]
["JAD X 3.18.08.71","JAD X 3.18.08.71"]
["JAD X 5.38","JAD X 5.38"]
["JAD 5.38.08.71","JAD 5.38.08.71"]
["JAD X 6.50","JAD X 6.50"]
["JAD X 6.50.10","JAD X 6.50.10"]
["JAD X 9.88","JAD X 9.88"]
["JAD X 9.88.10","JAD X 9.88.10"]
["JAD X 12.114","JAD X 12.114"]
["JAD X 12.114.10","JAD X 12.114.10"]
["JAD XK 2.11","JAD XK 2.11"]
["JAD XK 2.11.08.68","JAD XK 2.11.08.68"]
["JAD XK 3.18","JAD XK 3.18"]
["JAD XK 3.18.08.75","JAD XK 3.18.08.75"]
["JAD XK 5.38","JAD XK 5.38"]
["JAD XK 5.38.08.71","JAD XK 5.38.08.71"]
["JAD XK 6.50","JAD XK 6.50"]
["JAD XK 6.50.10","JAD XK 6.50.10"]
["JAD XK 6.50.08.72","JAD XK 6.50.08.72"]
["JAD XK 9.88","JAD XK 9.88"]
["JAD XK 9.88.10","JAD XK 9.88.10"]
["JAD XK 9.88.08.65","JAD XK 9.88.08.65"]
["JAD XK 9.88.08.85","JAD XK 9.88.08.85"]
["JAD XK 12.114","JAD XK 12.114"]
["JAD XK 12.114.10","JAD XK 12.114.10"]
["JAD XK 12.114.08.50","JAD XK 12.114.08.50"]
["JAD XK 12.114.08.60","JAD XK 12.114.08.60"]
["JAD XK 12.114.08.75","JAD XK 12.114.08.75"]
["JAD XK 17.217","JAD XK 17.217"]
["JAD XK 17.217.10","JAD XK 17.217.10"]
["LA12LN","LA12LN"]
["LA14LN","LA14LN"]
["LA22LN","LA22LN"]
["LA34LN","LA34LN"]
["LB31LN","LB31LN"]
["LB47LN","LB47LN"]
["LA60LN","LA60LN"]
["LC110LN","LC110LN"]
["LC170LN","LC170LN"]
["LD235LN","LD235LN"]
[]
[]
["temp","gęstość [kg/m3]"]
[55,985.73]
[60,983.2]
[65,980.59]
[70,977.81]
[75,974.84]
[80,971.8]
[85,968.6]
[90,965.3]
[95,961.9]
[100,958.34]
[105,954.71100000000001]
[110,950.96699999999998]
[115,947.10599999999999]
[120,943.12900000000002]
[125,939.03499999999997]
[130,934.82399999999996]
[135,930.495]
[140,926.05100000000004]
[145,921.49400000000003]
[150,916.82500000000005]
[]
[]
[]
[]
["ilość płyt"]
[6]
[8]
[10]
[12]
[14]
[16]
[18]
[20]
[22]
[24]
[26]
[28]
[30]
[32]
[34]
[36]
[38]
[40]
[42]
[44]
[46]
[48]
[50]
[52]
[54]
[56]
[58]
[60]
[62]
[64]
[66]
[68]
[70]
[72]
[74]
[76]
[78]
[80]
[82]
[84]
[86]
[88]
[90]
[92]
[94]
[96]
[98]
[100]
[102]
[104]
[106]
[108]
[110]
[112]
[114]
[116]
[118]
[120]
[122]
[124]
[126]
[128]
[130]
[132]
[134]
[136]
[138]
[140]
[142]
[144]
[146]
[148]
[150]
[152]
[154]
[156]
[158]
[160]
[162]
[164]
[166]
[168]
[170]
[172]
[174]
[176]
[178]
[180]
[182]
[184]
[186]
[188]
[190]
[192]
[194]
[196]
[198]
[200]
[202]
[204]
[206]
[208]
[210]
[212]
[214]
[216]
[218]
[220]
[222]
[224]
[226]
[228]
[230]
[232]
[234]
[236]
[238]
[240]
[242]
[244]
[246]
[248]
[250]
[252]
[254]
[256]
[258]
[260]
[262]
[264]
[266]
[268]
[270]
[272]
[274]
[276]
[278]
[280]
[282]
[284]
[286]
[288]
[290]
[292]
[294]
[296]
[298]
[300]
[302]
[304]
[306]
[308]
[310]
[312]
[314]
[316]
[318]
[320]
[322]
[324]
[326]
[328]
[330]
[332]
[334]
[336]
[338]
[340]
[342]
[344]
[346]
[348]
[350]
[352]
[354]
[356]
[358]
[360]
[362]
[364]
[366]
[368]
[370]
[372]
[374]
[376]
[378]
[380]
[382]
[384]
[386]
[388]
[390]
[392]
[394]
[396]
[398]
[400]

{"sheet":"ZB","index":9,"n_rows":304,"n_cols":9,"rows_kept":304,"cut":false,"hidden":true,"merged":[[2,8,2,20],[12,3,12,5]]}
[]
[null,null,null,"zawory bezpieczeństwa","HUSTY SYR","HUSTY SYR","cisnienia c.o.","cisnienia c.w.u."]
[null,null,null,null,"FLAMCO","ARMAK",2.5,4]
[null,null,null,null,"ARMAK",null,3,4.5]
[null,null,null,null,null,null,3.5,5]
[null,null,null,null,null,null,4,6]
[null,null,null,null,null,null,4.5,7]
[null,null,null,null,null,null,5,8]
[null,null,null,null,null,null,5.5,10]
[null,null,null,null,null,null,6]
[]
[]
[]
[]
["zawory na c.o."]
[]
[]
[null,null,null,"DN króćca wlotowego","do","p otw","wsp wypł alfa c",null,"złaczone teksty"]
[{"$f":"CONCATENATE(B19,\" dn\",D19,\" \",F19,\"bar\")","v":"husty syr dn25 2,5bar"},"husty syr",1915,25,20,2.5,0.41]
["husty syr dn32 2,5bar","husty syr",1915,32,27,2.5,0.35]
["husty syr dn40 2,5bar","husty syr",1915,40,35,2.5,0.45]
["husty syr dn50 2,5bar","husty syr",1915,50,42,2.5,0.28000000000000003]
["husty syr dn25 3bar","husty syr",1915,25,20,3,0.4]
["husty syr dn32 3bar","husty syr",1915,32,27,3,0.36]
["husty syr dn40 3bar","husty syr",1915,40,35,3,0.51]
["husty syr dn50 3bar","husty syr",1915,50,42,3,0.21]
["husty syr dn25 3,5bar","husty syr",1915,25,20,3.5,0.3]
["husty syr dn32 3,5bar","husty syr",1915,32,27,3.5,0.25]
["husty syr dn40 3,5bar","husty syr",1915,40,35,3.5,0.2]
["husty syr dn50 3,5bar","husty syr",1915,50,42,3.5,0.2]
["husty syr dn25 4bar","husty syr",1915,25,20,4,0.3]
["husty syr dn32 4bar","husty syr",1915,32,27,4,0.25]
["husty syr dn40 4bar","husty syr",1915,40,35,4,0.2]
["husty syr dn50 4bar","husty syr",1915,50,42,4,0.21]
["husty syr dn25 4,5bar","husty syr",1915,25,20,4.5,0.3]
["husty syr dn32 4,5bar","husty syr",1915,32,27,4.5,0.25]
["husty syr dn40 4,5bar","husty syr",1915,40,35,4.5,0.2]
["husty syr dn50 4,5bar","husty syr",1915,50,42,4.5,0.28000000000000003]
["husty syr dn25 5bar","husty syr",1915,25,20,5,0.41]
["husty syr dn32 5bar","husty syr",1915,32,27,5,0.36]
["husty syr dn40 5bar","husty syr",1915,40,35,5,0.26]
["husty syr dn50 5bar","husty syr",1915,50,42,5,0.28000000000000003]
["husty syr dn25 5,5bar","husty syr",1915,25,20,5.5,0.4]
["husty syr dn32 5,5bar","husty syr",1915,32,27,5.5,0.32]
["husty syr dn40 5,5bar","husty syr",1915,40,35,5.5,0.2]
["husty syr dn50 5,5bar","husty syr",1915,50,42,5.5,0.3]
["husty syr dn25 6bar","husty syr",1915,25,20,6,0.43]
["husty syr dn32 6bar","husty syr",1915,32,27,6,0.3]
["husty syr dn40 6bar","husty syr",1915,40,35,6,0.35]
["husty syr dn50 6bar","husty syr",1915,50,42,6,0.3]
["flamco dn25 2,5bar","flamco","Prescor",25,20,2.5,0.56000000000000005]
["flamco dn32 2,5bar","flamco","Prescor",32,25,2.5,0.33]
["flamco dn40 2,5bar","flamco","Prescor B",40,36,2.5,0.4]
["flamco dn50 2,5bar","flamco","Prescor B",50,44,2.5,0.4]
["flamco dn25 3bar","flamco","Prescor",25,20,3,0.46]
["flamco dn32 3bar","flamco","Prescor",32,25,3,0.5]
["flamco dn40 3bar","flamco","Prescor B",40,36,3,0.43]
["flamco dn50 3bar","flamco","Prescor B",50,44,3,0.32]
["flamco dn25 3,5bar","flamco","niestandardowe p1",25,20,3.5,"niestandardowe p1"]
["flamco dn32 3,5bar","flamco","niestandardowe p1",32,25,3.5,"niestandardowe p1"]
["flamco dn40 3,5bar","flamco","niestandardowe p1",40,36,3.5,"niestandardowe p1"]
["flamco dn50 3,5bar","flamco","niestandardowe p1",50,44,3.5,"niestandardowe p1"]
["flamco dn25 4bar","flamco","niestandardowe p1",25,20,4,"niestandardowe p1"]
["flamco dn32 4bar","flamco","niestandardowe p1",32,25,4,"niestandardowe p1"]
["flamco dn40 4bar","flamco","niestandardowe p1",40,36,4,"niestandardowe p1"]
["flamco dn50 4bar","flamco","niestandardowe p1",50,44,4,"niestandardowe p1"]
["flamco dn25 4,5bar","flamco","niestandardowe p1",25,20,4.5,"niestandardowe p1"]
["flamco dn32 4,5bar","flamco","niestandardowe p1",32,25,4.5,"niestandardowe p1"]
["flamco dn40 4,5bar","flamco","niestandardowe p1",40,36,4.5,"niestandardowe p1"]
["flamco dn50 4,5bar","flamco","niestandardowe p1",50,44,4.5,"niestandardowe p1"]
["flamco dn25 5bar","flamco","niestandardowe p1",25,20,5,"niestandardowe p1"]
["flamco dn32 5bar","flamco","niestandardowe p1",32,25,5,"niestandardowe p1"]
["flamco dn40 5bar","flamco","niestandardowe p1",40,36,5,"niestandardowe p1"]
["flamco dn50 5bar","flamco","niestandardowe p1",50,44,5,"niestandardowe p1"]
["flamco dn25 5,5bar","flamco","niestandardowe p1",25,20,5.5,"niestandardowe p1"]
["flamco dn32 5,5bar","flamco","niestandardowe p1",32,25,5.5,"niestandardowe p1"]
["flamco dn40 5,5bar","flamco","niestandardowe p1",40,36,5.5,"niestandardowe p1"]
["flamco dn50 5,5bar","flamco","niestandardowe p1",50,44,5.5,"niestandardowe p1"]
["flamco dn25 6bar","flamco","niestandardowe p1",25,20,6,"niestandardowe p1"]
["flamco dn32 6bar","flamco","niestandardowe p1",32,25,6,"niestandardowe p1"]
["flamco dn40 6bar","flamco","niestandardowe p1",40,36,6,"niestandardowe p1"]
["flamco dn50 6bar","flamco","niestandardowe p1",50,44,6,"niestandardowe p1"]
["armak dn20x32 2,5bar","armak","Si 6301","20x32",16,2.5,0.5]
["armak dn25x40 2,5bar","armak","Si 6301","25x40",20,2.5,0.5]
["armak dn32x50 2,5bar","armak","Si 6301","32x50",25,2.5,0.5]
["armak dn40x65 2,5bar","armak","Si 6301","40x65",32,2.5,0.5]
["armak dn50x80 2,5bar","armak","Si 6301","50x80",40,2.5,0.5]
["armak dn20x32 3bar","armak","Si 6301","20x32",16,3,0.5]
["armak dn25x40 3bar","armak","Si 6301","25x40",20,3,0.5]
["armak dn32x50 3bar","armak","Si 6301","32x50",25,3,0.5]
["armak dn40x65 3bar","armak","Si 6301","40x65",32,3,0.5]
["armak dn50x80 3bar","armak","Si 6301","50x80",40,3,0.5]
["armak dn20x32 3,5bar","armak","Si 6301","20x32",16,3.5,0.5]
["armak dn25x40 3,5bar","armak","Si 6301","25x40",20,3.5,0.5]
["armak dn32x50 3,5bar","armak","Si 6301","32x50",25,3.5,0.5]
["armak dn40x65 3,5bar","armak","Si 6301","40x65",32,3.5,0.5]
["armak dn50x80 3,5bar","armak","Si 6301","50x80",40,3.5,0.5]
["armak dn20x32 4bar","armak","Si 6301","20x32",16,4,0.5]
["armak dn25x40 4bar","armak","Si 6301","25x40",20,4,0.5]
["armak dn32x50 4bar","armak","Si 6301","32x50",25,4,0.5]
["armak dn40x65 4bar","armak","Si 6301","40x65",32,4,0.5]
["armak dn50x80 4bar","armak","Si 6301","50x80",40,4,0.5]
[{"$f":"CONCATENATE(B103,\" dn\",D103,\" \",F103,\"bar\")","v":"armak dn20x32 4,5bar"},"armak","Si 6301","20x32",16,4.5,0.5]
["armak dn25x40 4,5bar","armak","Si 6301","25x40",20,4.5,0.5]
["armak dn32x50 4,5bar","armak","Si 6301","32x50",25,4.5,0.5]
["armak dn40x65 4,5bar","armak","Si 6301","40x65",32,4.5,0.5]
["armak dn50x80 4,5bar","armak","Si 6301","50x80",40,4.5,0.5]
["armak dn20x32 5bar","armak","Si 6301","20x32",16,5,0.5]
["armak dn25x40 5bar","armak","Si 6301","25x40",20,5,0.5]
["armak dn32x50 5bar","armak","Si 6301","32x50",25,5,0.5]
["armak dn40x65 5bar","armak","Si 6301","40x65",32,5,0.5]
["armak dn50x80 5bar","armak","Si 6301","50x80",40,5,0.5]
["armak dn20x32 5,5bar","armak","niestandardowe p1","20x32",16,5.5,"niestandardowe p1"]
["armak dn25x40 5,5bar","armak","niestandardowe p1","25x40",20,5.5,"niestandardowe p1"]
["armak dn32x50 5,5bar","armak","niestandardowe p1","32x50",25,5.5,"niestandardowe p1"]
["armak dn40x65 5,5bar","armak","niestandardowe p1","40x65",32,5.5,"niestandardowe p1"]
["armak dn50x80 5,5bar","armak","niestandardowe p1","50x80",40,5.5,"niestandardowe p1"]
["armak dn20x32 6bar","armak","niestandardowe p1","20x32",16,6,"niestandardowe p1"]
["armak dn25x40 6bar","armak","niestandardowe p1","25x40",20,6,"niestandardowe p1"]
["armak dn32x50 6bar","armak","niestandardowe p1","32x50",25,6,"niestandardowe p1"]
["armak dn40x65 6bar","armak","niestandardowe p1","40x65",32,6,"niestandardowe p1"]
["armak dn50x80 6bar","armak","niestandardowe p1","50x80",40,6,"niestandardowe p1"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["zawory na c.w.u."]
[null,null,null,"DN króćca wlotowego","do","p otw","wsp wypł alfa c"]
[{"$f":"CONCATENATE(B135,\" dn\",D135,\" \",F135,\"bar\")","v":"husty syr dn20 4bar"},"husty syr",2115,20,14,4,0.55000000000000004]
["husty syr dn25 4bar","husty syr",2115,25,20,4,0.54]
["husty syr dn32 4bar","husty syr",2115,32,27,4,0.48]
["husty syr dn40 4bar","husty syr",2115,40,35,4,0.53]
["husty syr dn50 4bar","husty syr",2115,50,42,4,0.55000000000000004]
["husty syr dn20 4,5bar","husty syr",2115,20,14,4.5,0.55000000000000004]
["husty syr dn25 4,5bar","husty syr",2115,25,20,4.5,0.54]
["husty syr dn32 4,5bar","husty syr",2115,32,27,4.5,0.48]
["husty syr dn40 4,5bar","husty syr",2115,40,35,4.5,0.53]
["husty syr dn50 4,5bar","husty syr",2115,50,42,4.5,0.55000000000000004]
["husty syr dn20 5bar","husty syr",2115,20,14,5,0.55000000000000004]
["husty syr dn25 5bar","husty syr",2115,25,20,5,0.54]
["husty syr dn32 5bar","husty syr",2115,32,27,5,0.48]
["husty syr dn40 5bar","husty syr",2115,40,35,5,0.53]
["husty syr dn50 5bar","husty syr",2115,50,42,5,0.55000000000000004]
["husty syr dn20 6bar","husty syr",2115,20,14,6,0.55000000000000004]
["husty syr dn25 6bar","husty syr",2115,25,20,6,0.54]
["husty syr dn32 6bar","husty syr",2115,32,27,6,0.48]
["husty syr dn40 6bar","husty syr",2115,40,35,6,0.53]
["husty syr dn50 6bar","husty syr",2115,50,42,6,0.55000000000000004]
["husty syr dn20 7bar","husty syr",2115,20,14,7,0.55000000000000004]
["husty syr dn25 7bar","husty syr",2115,25,20,7,0.54]
["husty syr dn32 7bar","husty syr",2115,32,27,7,0.48]
["husty syr dn40 7bar","husty syr",2115,40,35,7,0.53]
["husty syr dn50 7bar","husty syr",2115,50,42,7,0.55000000000000004]
["husty syr dn20 8bar","husty syr",2115,20,14,8,0.55000000000000004]
["husty syr dn25 8bar","husty syr",2115,25,20,8,0.54]
["husty syr dn32 8bar","husty syr",2115,32,27,8,0.48]
["husty syr dn40 8bar","husty syr",2115,40,35,8,0.53]
["husty syr dn50 8bar","husty syr",2115,50,42,8,0.55000000000000004]
["husty syr dn20 10bar","husty syr",2115,20,14,10,0.55000000000000004]
["husty syr dn25 10bar","husty syr",2115,25,20,10,0.54]
["husty syr dn32 10bar","husty syr",2115,32,27,10,0.48]
["husty syr dn40 10bar","husty syr",2115,40,35,10,0.53]
["husty syr dn50 10bar","husty syr",2115,50,42,10,0.55000000000000004]
["armak dn20x32 4bar","armak",775,"20x32",16,4,0.78]
["armak dn25x40 4bar","armak",775,"25x40",20,4,0.78]
["armak dn32x50 4bar","armak",775,"32x50",25,4,0.78]
["armak dn20x32 4,5bar","armak",775,"20x32",16,4.5,0.78]
["armak dn25x40 4,5bar","armak",775,"25x40",20,4.5,0.78]
["armak dn32x50 4,5bar","armak",775,"32x50",25,4.5,0.78]
["armak dn20x32 5bar","armak",775,"20x32",16,5,0.78]
["armak dn25x40 5bar","armak",775,"25x40",20,5,0.78]
["armak dn32x50 5bar","armak",775,"32x50",25,5,0.78]
["armak dn20x32 6bar","armak",775,"20x32",16,6,0.78]
["armak dn25x40 6bar","armak",775,"25x40",20,6,0.78]
["armak dn32x50 6bar","armak",775,"32x50",25,6,0.78]
["armak dn20x32 7bar","armak",775,"20x32",16,7,0.78]
["armak dn25x40 7bar","armak",775,"25x40",20,7,0.78]
["armak dn32x50 7bar","armak",775,"32x50",25,7,0.78]
["armak dn20x32 8bar","armak",775,"20x32",16,8,0.78]
["armak dn25x40 8bar","armak",775,"25x40",20,8,0.78]
["armak dn32x50 8bar","armak",775,"32x50",25,8,0.78]
["armak dn20x32 10bar","armak",775,"20x32",16,10,0.78]
["armak dn25x40 10bar","armak",775,"25x40",20,10,0.78]
["armak dn32x50 10bar","armak",775,"32x50",25,10,0.78]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,"LSL0/LSK0",70]
[null,null,null,"LSL1/LSK1",180]
[null,null,null,"LSL2/LSK2",176]
[null,null,null,"LSL3/LSK3",142]
[null,null,null,"LSL4/LSK4",198]
[null,null,null,"LSL5/LSK5",172]

{"sheet":"NWP","index":10,"n_rows":110,"n_cols":19,"rows_kept":110,"cut":false,"hidden":true,"merged":[]}
[]
[]
[]
[null,"Producenci",null,"REFLEX",null,null,"Tz ","gęstość wody","tz-t1","dV"]
[null,null,null,"FLAMCO typ C",null,null,"C","kg/m3","K","dm3/kg"]
[null,null,null,"FLAMCO typ K",null,null,100,958.3,{"$f":"G6-10","v":90},4.3200000000000002E-2]
[null,null,null,"CIMM",null,null,95,961.9,{"$f":"G7-10","v":85},3.9300000000000002E-2]
[null,null,null,"VAREM",null,null,90,965.3,80,3.56E-2]
[null,null,null,"FERRO",null,null,85,968.6,75,3.2099999999999997E-2]
[null,null,null,null,null,null,80,971.8,70,2.87E-2]
[null,null,null,null,null,null,75,974.8,65,2.5600000000000001E-2]
[null,null,null,null,null,null,70,977.8,60,2.24E-2]
[null,null,null,null,null,null,65,980.5,55,1.9599999999999999E-2]
[null,null,null,null,null,null,60,983.2,50,1.6799999999999999E-2]
[null,null,null,null,null,null,55,985.73,45,{"$f":"1.42*10^(-2)","v":1.4199999999999999E-2}]
[null,null,null,null,null,null,50,988.1,40,{"$f":"1.18*10^(-2)","v":1.18E-2}]
[null,null,null,null,null,null,10,999.7,0]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"Vn bez rezerwy",null,null,null,"Vn z rezerwa"]
[null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'PN-NWP'!E43","v":{"$error":"#N/A"}},null,null,null,197.71548001200367]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"pojemność naczynia"]
[null,"producent","typ","pojemność","wysokość","średnica","cisnienie robocze","średnica podłaczenia",null,"cisnienie wstepne"]
[{"$f":"CONCATENATE(B28,D28)","v":"REFLEX12"},"REFLEX","NG",12,315,272,3,20,null,1.5,null,null,{"$f":"D28-M$23","v":{"$error":"#N/A"}},{"$f":"IF(M28>=0,D28,IF(M29>=0,D29,IF(M30>=0,D30,IF(M31>=0,D31,IF(M32>=0,D32,IF(M33>=0,D33,IF(M34>=0,D34,IF(M35>=0,D35,\"-\"))))))))","v":{"$error":"#N/A"}},{"$f":"IF(N$28 = \"-\",N36,N28)","v":{"$error":"#N/A"}},null,{"$f":"D28-Q$23","v":-185.71548001200367},{"$f":"IF(Q28>=0,D28,IF(Q29>=0,D29,IF(Q30>=0,D30,IF(Q31>=0,D31,IF(Q32>=0,D32,IF(Q33>=0,D33,IF(Q34>=0,D34,IF(Q35>=0,D35,\"-\"))))))))","v":"-"},{"$f":"IF(R$28 = \"-\",R36,R28)","v":200}]
[{"$f":"CONCATENATE(B29,D29)","v":"REFLEX18"},"REFLEX","NG",18,360,308,3,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,{"$f":"D29-Q$23","v":-179.71548001200367}]
["REFLEX25","REFLEX","NG",25,480,308,3,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-172.71548001200367]
["REFLEX35","REFLEX","NG",35,465,375,3,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-162.71548001200367]
["REFLEX50","REFLEX","NG",50,495,441,6,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-147.71548001200367]
["REFLEX80","REFLEX","NG",80,570,512,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-117.71548001200367]
["REFLEX100","REFLEX","NG",100,680,512,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-97.715480012003667]
["REFLEX140","REFLEX","NG",140,890,512,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-57.715480012003667]
["REFLEX200","REFLEX","N",200,785,634,6,25,null,1.5,null,null,{"$error":"#N/A"},{"$f":"IF(M36>=0,D36,IF(M37>=0,D37,IF(M38>=0,D38,IF(M39>=0,D39,IF(M40>=0,D40,IF(M41>=0,D41,IF(M42>=0,D42,IF(M43>=0,D43,\"-\"))))))))","v":{"$error":"#N/A"}},null,null,2.2845199879963332,{"$f":"IF(Q36>=0,D36,IF(Q37>=0,D37,IF(Q38>=0,D38,IF(Q39>=0,D39,IF(Q40>=0,D40,IF(Q41>=0,D41,IF(Q42>=0,D42,IF(Q43>=0,D43,\"-\"))))))))","v":200}]
["REFLEX250","REFLEX","N",250,915,634,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,52.284519987996333]
["REFLEX300","REFLEX","N",300,1085,634,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,102.28451998799633]
["REFLEX400","REFLEX","N",400,1075,740,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,202.28451998799633]
["REFLEX500","REFLEX","N",500,1295,740,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,302.2845199879963]
["REFLEX600","REFLEX","N",600,1530,740,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,402.2845199879963]
["REFLEX800","REFLEX","N",800,1990,740,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,602.2845199879963]
["REFLEX1000","REFLEX","N",1000,2430,740,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,802.2845199879963]
[{"$f":"CONCATENATE(B44,\" typ C\",D44)","v":"FLAMCO typ C12"},"FLAMCO","Flexcon C ",12,330,286,3,20,null,1.5,null,null,{"$error":"#N/A"},{"$f":"IF(M44>=0,D44,IF(M45>=0,D45,IF(M46>=0,D46,IF(M47>=0,D47,IF(M48>=0,D48,IF(M49>=0,D49,IF(M50>=0,D50,IF(M51>=0,D51,\"-\"))))))))","v":{"$error":"#N/A"}},{"$f":"IF(N$44 = \"-\",N52,N44)","v":{"$error":"#N/A"}},null,-185.71548001200367,{"$f":"IF(Q44>=0,D44,IF(Q45>=0,D45,IF(Q46>=0,D46,IF(Q47>=0,D47,IF(Q48>=0,D48,IF(Q49>=0,D49,IF(Q50>=0,D50,IF(Q51>=0,D51,\"-\"))))))))","v":"-"},{"$f":"IF(R$44 = \"-\",R52,R44)","v":200}]
[{"$f":"CONCATENATE(B45,\" typ C\",D45)","v":"FLAMCO typ C18"},"FLAMCO","Flexcon C ",18,325,328,3,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-179.71548001200367]
["FLAMCO typ C25","FLAMCO","Flexcon C ",25,375,358,3,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-172.71548001200367]
["FLAMCO typ C35","FLAMCO","Flexcon C ",35,426,396,3,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-162.71548001200367]
["FLAMCO typ C50","FLAMCO","Flexcon C ",50,488,437,3,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-147.71548001200367]
["FLAMCO typ C80","FLAMCO","Flexcon C ",80,555,519,3,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-117.71548001200367]
["FLAMCO typ C110","FLAMCO","Flexcon C ",110,696,519,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-87.715480012003667]
["FLAMCO typ C140","FLAMCO","Flexcon C ",140,950,519,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-57.715480012003667]
["FLAMCO typ C200","FLAMCO","Flexcon C ",200,1294,484,6,25,null,1.5,null,null,{"$error":"#N/A"},{"$f":"IF(M52>=0,D52,IF(M53>=0,D53,IF(M54>=0,D54,IF(M55>=0,D55,IF(M56>=0,D56,IF(M57>=0,D57,\"-\"))))))","v":{"$error":"#N/A"}},null,null,2.2845199879963332,{"$f":"IF(Q52>=0,D52,IF(Q53>=0,D53,IF(Q54>=0,D54,IF(Q55>=0,D55,IF(Q56>=0,D56,IF(Q57>=0,D57,\"-\"))))))","v":200}]
["FLAMCO typ C300","FLAMCO","Flexcon C ",300,1328,600,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,102.28451998799633]
["FLAMCO typ C425","FLAMCO","Flexcon C ",425,1178,790,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,227.28451998799633]
["FLAMCO typ C600","FLAMCO","Flexcon C ",600,1538,790,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,402.2845199879963]
["FLAMCO typ C800","FLAMCO","Flexcon C ",800,1888,790,6,25,null,1,null,null,{"$error":"#N/A"},null,null,null,602.2845199879963]
["FLAMCO typ C1000","FLAMCO","Flexcon C ",1000,2268,790,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,802.2845199879963]
[{"$f":"CONCATENATE(B58,\" typ K\",D58)","v":"FLAMCO typ K110"},"FLAMCO","Flexcon K ",110,784,484,6,25,null,3,null,null,{"$error":"#N/A"},{"$f":"IF(M58>=0,D58,IF(M59>=0,D59,IF(M60>=0,D60,IF(M61>=0,D61,IF(M62>=0,D62,IF(M63>=0,D63,IF(M64>=0,D64,IF(M65>=0,D65,\"-\"))))))))","v":{"$error":"#N/A"}},{"$f":"N58","v":{"$error":"#N/A"}},null,-87.715480012003667,{"$f":"IF(Q58>=0,D58,IF(Q59>=0,D59,IF(Q60>=0,D60,IF(Q61>=0,D61,IF(Q62>=0,D62,IF(Q63>=0,D63,IF(Q64>=0,D64,IF(Q65>=0,D65,\"-\"))))))))","v":200},{"$f":"R58","v":200}]
[{"$f":"CONCATENATE(B59,\" typ K\",D59)","v":"FLAMCO typ K140"},"FLAMCO","Flexcon K ",140,950,484,6,25,null,3,null,null,{"$error":"#N/A"},null,null,null,-57.715480012003667]
["FLAMCO typ K200","FLAMCO","Flexcon K ",200,960,600,6,25,null,3,null,null,{"$error":"#N/A"},null,null,null,2.2845199879963332]
["FLAMCO typ K300","FLAMCO","Flexcon K ",300,1330,600,6,25,null,3,null,null,{"$error":"#N/A"},null,null,null,102.28451998799633]
["FLAMCO typ K425","FLAMCO","Flexcon K ",425,1180,790,6,25,null,3,null,null,{"$error":"#N/A"},null,null,null,227.28451998799633]
["FLAMCO typ K600","FLAMCO","Flexcon K ",600,1540,790,6,25,null,3,null,null,{"$error":"#N/A"},null,null,null,402.2845199879963]
["FLAMCO typ K800","FLAMCO","Flexcon K ",800,1890,790,6,25,null,3,null,null,{"$error":"#N/A"},null,null,null,602.2845199879963]
["FLAMCO typ K1000","FLAMCO","Flexcon K ",1000,2270,790,6,25,null,3,null,null,{"$error":"#N/A"},null,null,null,802.2845199879963]
["CIMM6","CIMM","ER",6,245,245,5,20,null,1.5,null,null,{"$error":"#N/A"},{"$f":"IF(M66>=0,D66,IF(M67>=0,D67,IF(M68>=0,D68,IF(M69>=0,D69,IF(M70>=0,D70,IF(M71>=0,D71,IF(M72>=0,D72,IF(M73>=0,D73,\"-\"))))))))","v":{"$error":"#N/A"}},{"$f":"IF(N66=\"-\",IF(N74=\"-\",N82,N74),N66)","v":{"$error":"#N/A"}},null,-191.71548001200367,{"$f":"IF(Q66>=0,D66,IF(Q67>=0,D67,IF(Q68>=0,D68,IF(Q69>=0,D69,IF(Q70>=0,D70,IF(Q71>=0,D71,IF(Q72>=0,D72,IF(Q73>=0,D73,\"-\"))))))))","v":"-"},{"$f":"IF(R66=\"-\",IF(R74=\"-\",R82,R74),R66)","v":200}]
["CIMM8","CIMM","ER",8,275,245,5,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-189.71548001200367]
["CIMM10","CIMM","ER",10,325,245,5,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-187.71548001200367]
[{"$f":"CONCATENATE(B69,D69)","v":"CIMM12"},"CIMM","ER",12,320,285,5,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-185.71548001200367]
["CIMM14","CIMM","ER",14,345,285,5,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-183.71548001200367]
["CIMM18","CIMM","ER",18,385,285,5,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-179.71548001200367]
["CIMM24","CIMM","ER",24,420,325,5,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-173.71548001200367]
["CIMM35","CIMM","ERE",35,475,380,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-162.71548001200367]
["CIMM50","CIMM","ERE",50,595,380,6,25,null,1.5,null,null,{"$error":"#N/A"},{"$f":"IF(M74>=0,D74,IF(M75>=0,D75,IF(M76>=0,D76,IF(M77>=0,D77,IF(M78>=0,D78,IF(M79>=0,D79,IF(M80>=0,D80,IF(M81>=0,D81,\"-\"))))))))","v":{"$error":"#N/A"}},null,null,-147.71548001200367,{"$f":"IF(Q74>=0,D74,IF(Q75>=0,D75,IF(Q76>=0,D76,IF(Q77>=0,D77,IF(Q78>=0,D78,IF(Q79>=0,D79,IF(Q80>=0,D80,IF(Q81>=0,D81,\"-\"))))))))","v":200}]
["CIMM80","CIMM","ERE",80,620,460,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-117.71548001200367]
["CIMM100","CIMM","ERE",100,810,460,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-97.715480012003667]
["CIMM150","CIMM","ERE",150,970,510,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-47.715480012003667]
["CIMM200","CIMM","ERE",200,1000,590,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,2.2845199879963332]
["CIMM250","CIMM","ERE",250,1230,590,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,52.284519987996333]
["CIMM300","CIMM","ERE",300,1220,650,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,102.28451998799633]
["CIMM400","CIMM","ERE",400,1250,750,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,202.28451998799633]
["CIMM500","CIMM","ERE",500,1480,750,6,25,null,1.5,null,null,{"$error":"#N/A"},{"$f":"IF(M82>=0,D82,IF(M83>=0,D83,IF(M84>=0,D84,IF(M85>=0,D85,IF(M86>=0,D86,\"-\")))))","v":{"$error":"#N/A"}},null,null,302.2845199879963,{"$f":"IF(Q82>=0,D82,IF(Q83>=0,D83,IF(Q84>=0,D84,IF(Q85>=0,D85,IF(Q86>=0,D86,\"-\")))))","v":500}]
["CIMM600","CIMM","ERE",600,1640,750,6,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,402.2845199879963]
["CIMM750","CIMM","ERE",750,1820,800,8,50,null,2.5,null,null,{"$error":"#N/A"},null,null,null,552.2845199879963]
["CIMM1000","CIMM","ERE",1000,2130,800,8,65,null,2.5,null,null,{"$error":"#N/A"},null,null,null,802.2845199879963]
["CIMM1500","CIMM","ERE",1500,2130,1000,8,65,null,2.5,null,null,{"$error":"#N/A"},null,null,null,1302.2845199879964]
["VAREM25","VAREM","Extravarem LR ",25,500,290,5,20,null,1,null,null,{"$error":"#N/A"},{"$f":"IF(M87>=0,D87,IF(M88>=0,D88,IF(M89>=0,D89,IF(M90>=0,D90,IF(M91>=0,D91,IF(M92>=0,D92,IF(M93>=0,D93,IF(M94>=0,D94,\"-\"))))))))","v":{"$error":"#N/A"}},{"$f":"N87","v":{"$error":"#N/A"}},null,-172.71548001200367,{"$f":"IF(Q87>=0,D87,IF(Q88>=0,D88,IF(Q89>=0,D89,IF(Q90>=0,D90,IF(Q91>=0,D91,IF(Q92>=0,D92,IF(Q93>=0,D93,IF(Q94>=0,D94,\"-\"))))))))","v":200},{"$f":"R87","v":200}]
["VAREM40","VAREM","Extravarem LR",40,610,320,5,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-157.71548001200367]
["VAREM80","VAREM","Maxivarem LR ",80,695,450,4.9000000000000004,20,null,2,null,null,{"$error":"#N/A"},null,null,null,-117.71548001200367]
["VAREM100","VAREM","Maxivarem LR ",100,760,450,4.9000000000000004,25,null,2,null,null,{"$error":"#N/A"},null,null,null,-97.715480012003667]
["VAREM150","VAREM","Maxivarem LR ",150,785,550,4.9000000000000004,25,null,2,null,null,{"$error":"#N/A"},null,null,null,-47.715480012003667]
["VAREM200","VAREM","Maxivarem LR ",200,1000,550,4.9000000000000004,32,null,2,null,null,{"$f":"D92-M$23","v":{"$error":"#N/A"}},null,null,null,2.2845199879963332]
[{"$f":"CONCATENATE(B93,D93)","v":"VAREM250"},"VAREM","Maxivarem LR",250,1000,630,6,32,null,2.5,null,null,{"$error":"#N/A"},null,null,null,{"$f":"D93-Q$23","v":52.284519987996333}]
[{"$f":"CONCATENATE(B94,D94)","v":"VAREM300"},"VAREM","Maxivarem LR ",300,1180,630,6,32,null,2.5,null,null,{"$error":"#N/A"},null,null,null,{"$f":"D94-Q$23","v":102.28451998799633}]
[{"$f":"CONCATENATE(B95,D95)","v":"FERRO5"},"FERRO","CO5W",5,304,160,8,20,null,1.5,null,null,{"$error":"#N/A"},{"$f":"IF(M95>=0,D95,IF(M96>=0,D96,IF(M97>=0,D97,IF(M98>=0,D98,IF(M99>=0,D99,IF(M100>=0,D100,IF(M101>=0,D101,IF(M102>=0,D102,\"-\"))))))))","v":{"$error":"#N/A"}},{"$f":"IF(N$95 = \"-\",N103,N95)","v":{"$error":"#N/A"}},null,{"$f":"D95-Q$23","v":-192.71548001200367},{"$f":"IF(Q95>=0,D95,IF(Q96>=0,D96,IF(Q97>=0,D97,IF(Q98>=0,D98,IF(Q99>=0,D99,IF(Q100>=0,D100,IF(Q101>=0,D101,IF(Q102>=0,D102,\"-\"))))))))","v":"-"},{"$f":"IF(R$95 = \"-\",R103,R95)","v":200}]
[{"$f":"CONCATENATE(B96,D96)","v":"FERRO8"},"FERRO","CO8W",8,316,200,8,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-189.71548001200367]
["FERRO12","FERRO","CO12W",12,295,280,8,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-185.71548001200367]
["FERRO18","FERRO","CO18W",18,456,280,8,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-179.71548001200367]
["FERRO24","FERRO","CO24W",24,489,280,8,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-173.71548001200367]
["FERRO35","FERRO","CO35S",35,450,365,8,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-162.71548001200367]
["FERRO35","FERRO","CO35W",35,440,365,8,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-162.71548001200367]
["FERRO50","FERRO","CO50S",50,564,365,8,25,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-147.71548001200367]
["FERRO50","FERRO","CO50W",50,545,365,8,25,null,1.5,null,null,{"$error":"#N/A"},{"$f":"IF(M103>=0,D103,IF(M104>=0,D104,IF(M105>=0,D105,IF(M106>=0,D106,IF(M107>=0,D107,IF(M108>=0,D108,IF(M109>=0,D109,IF(M110>=0,D110,\"-\"))))))))","v":{"$error":"#N/A"}},null,null,-147.71548001200367,{"$f":"IF(Q103>=0,D103,IF(Q104>=0,D104,IF(Q105>=0,D105,IF(Q106>=0,D106,IF(Q107>=0,D107,IF(Q108>=0,D108,IF(Q109>=0,D109,IF(Q110>=0,D110,\"-\"))))))))","v":200}]
["FERRO60","FERRO","CO60S",60,668,365,8,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-137.71548001200367]
["FERRO80","FERRO","CO80S",80,687,410,8,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-117.71548001200367]
["FERRO100","FERRO","CO100S",100,663,495,8,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-97.715480012003667]
["FERRO150","FERRO","CO150S",150,795,550,8,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,-47.715480012003667]
["FERRO200","FERRO","CO200S",200,1085,600,8,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,2.2845199879963332]
["FERRO250","FERRO","CO250S",250,1051,650,8,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,52.284519987996333]
["FERRO300","FERRO","CO300S",300,1212,650,8,20,null,1.5,null,null,{"$error":"#N/A"},null,null,null,102.28451998799633]

{"sheet":"gestosc wody","index":11,"n_rows":19,"n_cols":4,"rows_kept":19,"cut":false,"hidden":true,"merged":[]}
[]
[null,"ciepło właściwe wody",4.1900000000000004,"kJ/K*kg"]
[null,"przyśpieszenie ziemskie",9.81,"m/s2"]
[null,"Gęstość wody dla:"]
[null,30,995.67,"kg/m3"]
[null,35,994.06,"kg/m3"]
[null,40,992.24,"kg/m3"]
[null,45,990.25,"kg/m3"]
[null,50,988.07,"kg/m3"]
[null,55,985.73,"kg/m3"]
[null,60,983.24,"kg/m3"]
[null,65,980.59,"kg/m3"]
[null,70,977.81,"kg/m3"]
[null,75,974.89,"kg/m3"]
[null,80,971.83,"kg/m3"]
[null,85,968.65,"kg/m3"]
[null,90,965.34,"kg/m3"]
[null,95,961.92,"kg/m3"]
[null,100,958.38,"kg/m3"]